## BoQ1
Government eProcurement System Created By: Sachin Khangar Created Date/Time: 16-Sep-2026 05:51 PM Tender Title: SITC of New LED light fittings and associated Electrical Works at Vadodara Airport Tender ID: 2026_AAI_285496_1
Tender Inviting Authority: Jt.Gen.Manager(E-E), AAI, CA, Vadodara
Name of Work :- SITC of New LED light fittings and associated Electrical Works at Vadodara Airport.
Contract No: AAI/WR/VADO/E-E/NIT-04/SITC OF LED/2026-27
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Instapower Ltd (GSTN-05AAACI9712L1ZG) BID ID -1056312 |  | SYNERGY LIGHTING SOLUTIONS (GSTN-NA) BID ID -1063066 |  | Krishsons International Engineers And Consultants (I) Pvt. Ltd (GSTN-NA) BID ID -1062658 |  | KIVASA GLOBALTECH PVT LTD (GSTN-NA) BID ID -1052461
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I, Supply of LED fittings & Fans Supply of 2’x2’ recessed mounted backlit LED troffer luminaire with system wattage ≥ 36W and system lumen efficacy ≥140 lm/W.The luminaire shall be constructed from CRCA sheet steel housing with high-quality white powder-coated finish, complete with high transmittivity opal white diffuser to ensure low glare and uniform light distribution. The fixture shall be sleek in design with a minimum depth of 35 mm.The luminaire shall have CRI ≥80, SDCM ≤5, and CCT of 5700 - 6500K. The rated life shall be L70 ≥50,000 hours.Electrical parameters shall include power factor ≥0.95, THD ≤10%, suitable for an operating voltage range of 140–270 VAC, 50 Hz, with inbuilt surge protection of minimum 4 kV.The LED driver shall be EMI/EMC compliant, isolated type, with efficiency ≥85%, and shall include protections against short circuit, open circuit, along with P2P protection up to 440V for minimum 4 hours, and low/high voltage cutoff with auto recovery feature.The fixture shall operate within a temperature range of -10°C to +45°C and shall comply with Electrical Class I protection, IP40 ingress protection, and IK03 impact rating.The thermal management shall be ensured through an efficient aluminium heat sink design, maintaining LED junction temperature below 90°C.The maximum power consumption shall not exceed the specified rating. The luminaire and driver shall be BIS compliant, and valid certificates shall be submitted. LM-79, LM-80, and TTR reports from NABL accredited laboratories shall also be provided.The luminaire and lighting performance shall comply with relevant provisions of IS 10322.The manufacturer’s name/logo shall be engraved/ embossed/ screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM | 185.00 | Nos. |  | 1430.00 | 264550.00 | 1550.00 | 286750.00 | 1300.00 | 240500.00 | 1275.00 | 235875.00 | 235875.00 | KIVASA GLOBALTECH PVT LTD
2.00 | Supply of 1’x4’ recessed mounted backlit LED troffer luminaire with system wattage ≥ 36W and system lumen efficacy ≥120 lm/W.The luminaire shall be constructed from CRCA sheet steel housing with high-quality white powder-coated finish, complete with high transmittivity opal white diffuser to ensure low glare and uniform light distribution. The fixture shall be sleek in design with a minimum depth of 35 mm.The luminaire shall have CRI ≥80, SDCM ≤5, and CCT of 5700 - 6500K. The rated life shall be L70 ≥50,000 hours.Electrical parameters shall include power factor ≥0.95, THD ≤10%, suitable for an operating voltage range of 140–270 VAC, 50 Hz, with inbuilt surge protection of minimum 4 kV.The LED driver shall be EMI/EMC compliant, isolated type, with efficiency ≥85%, and shall include protections against short circuit, open circuit, along with P2P protection up to 440V for minimum 4 hours, and low/high voltage cutoff with auto recovery feature.The fixture shall operate within a temperature range of -10°C to +45°C and shall comply with Electrical Class I protection, IP20 ingress protection, and IK03 impact rating.The thermal management shall be ensured through an efficient aluminium heat sink design, maintaining LED junction temperature below 90°C.The maximum power consumption shall not exceed the specified rating. The luminaire and driver shall be BIS compliant, and valid certificates shall be submitted. LM-79, LM-80, and TTR reports from NABL accredited laboratories shall also be provided.The luminaire and lighting performance shall comply with relevant provisions of IS 10322.The manufacturer’s name/logo shall be engraved/ embossed/ screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive OEM warranty. | 395.00 | Nos. |  | 1573.00 | 621335.00 | 1650.00 | 651750.00 | 1850.00 | 730750.00 | 1530.00 | 604350.00 | 604350.00 | KIVASA GLOBALTECH PVT LTD
3.00 | Supply of LED surface mounted batten luminaire with system wattage ≥ 20W. Fixture to be made of extruded aluminium housing with high transmittivity PMMA/PC inset diffuser for low glare and uniform light distribution. System luminous efficacy ≥120 lm/W, CRI ≥80, SDCM ≤5, and CCT of 5700 - 6500K. The rated life shall be L70 ≥50,000 hours.Electrical parameters shall include power factor ≥0.95, THD ≤10%, suitable for an operating voltage range of 140–270 VAC, 50 Hz, with inbuilt surge protection of minimum 4 kV.The LED driver shall have efficiency ≥85% and shall include short circuit and open circuit protection.The fixture shall operate within a temperature range of -10°C to +45°C and shall comply with Electrical Class I protection, IP20 ingress protection, and IK04 impact rating.The thermal management shall be ensured through an efficient aluminium heat sink design, maintaining LED junction temperature below 90°C.The maximum power consumption shall not exceed the specified rating. The luminaire and driver shall be BIS compliant, and valid certificates shall be submitted. LM-79, LM-80, and TTR reports from NABL accredited laboratories shall also be provided.The luminaire and lighting performance shall comply with relevant provisions of IS 10322. The manufacturer’s name/logo shall be engraved/ embossed/ screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 255.00 | Nos. |  | 679.25 | 173208.75 | 250.00 | 63750.00 | 380.00 | 96900.00 | 305.00 | 77775.00 | 63750.00 | SYNERGY LIGHTING SOLUTIONS
4.00 | Supply of LED surface mounted batten luminaire with system wattage not exceeding 40W. Fixture to be made of extruded aluminium housing with high transmittivity PMMA/PC inset diffuser for low glare and uniform light distribution.The luminaire shall have minimum system lumen output of 4800 lumens with system luminous efficacy ≥120 lm/W, CRI ≥80, SDCM ≤5, and CCT of 5700 - 6500K. The rated life shall be L70 ≥50,000 hours.Electrical parameters shall include power factor ≥0.95, THD ≤10%, suitable for an operating voltage range of 140–270 VAC, 50 Hz, with inbuilt surge protection of minimum 4 kV.The LED driver shall have efficiency ≥85% and shall include short circuit and open circuit protection.The fixture shall operate within a temperature range of -10°C to +45°C and shall comply with Electrical Class I protection, IP20 ingress protection, and IK04 impact rating.The thermal management shall be ensured through an efficient aluminium heat sink design, maintaining LED junction temperature below 90°C.The maximum power consumption shall not exceed the specified rating. The luminaire and driver shall be BIS compliant, and valid certificates shall be submitted. LM-79, LM-80, and TTR reports from NABL accredited laboratories shall also be provided.The luminaire and lighting performance shall comply with relevant provisions of IS 10322.The manufacturer’s name/logo shall be engraved/ embossed/ screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 560.00 | Nos. |  | 2145.00 | 1201200.00 | 450.00 | 252000.00 | 550.00 | 308000.00 | 320.00 | 179200.00 | 179200.00 | KIVASA GLOBALTECH PVT LTD
5.00 | Supply of non-flammable LED weatherproof batten luminaire suitable for CISF Armoury application with system wattage ≥36W and system luminous efficacy ≥135 lm/W. Luminaire shall be provided with flame-retardant and self-extinguishing housing and diffuser conforming to UL94 V-0 or equivalent standard, CRI ≥80, SDCM ≤5, CCT 6500K, rated life L70 ≥50,000 burning hours, PF ≥0.95, THD <10%, driver efficiency ≥85%, operating voltage 120–300V AC and surge protection minimum DM-4kV and CM-3kV. The luminaire shall be IP66 and IK10 rated and suitable for industrial indoor applications. Luminaire and driver shall be BIS compliant and valid LM-79, LM-80 and NABL accredited test reports shall be submitted. The luminaire shall comply with IS 10322 and The manufacturer’s name/logo shall be engraved/ embossed/ screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 15.00 | Nos. |  | 643.50 | 9652.50 | 400.00 | 6000.00 | 650.00 | 9750.00 | 1275.00 | 19125.00 | 6000.00 | SYNERGY LIGHTING SOLUTIONS
6.00 | Supply of terminal building canopy edge light , Wattage ≥ 90W, luminous efficacy >125 lm/W, operating voltage 120–300V, rated voltage 220–240V, frequency 50 Hz, with surge arrestor more than or equal 4 kV inbuilt in driver and 10 kV external inside housing, driver efficiency >85%, CCT 5700 - 6500°K ,THD <10% as per IEC 61000‑3‑2, PF ≥0.95, IP‑66, IK‑08, CRI >70,SDCM ≤5, rated life L70 ≥50,000 burning hours, under/over‑voltage protection, short‑circuit and open‑circuit protection, EMI‑EMC compliance as per CISPR‑15,suitable for outdoor canopy edge illumination, complete with constant‑current driver and The manufacturer’s name/logo shall be engraved/ embossed/ screen-printed on the luminaire housing.Luminaire and driver shall be BIS compliant and valid certificates shall be submitted. Valid LM-79, LM-80 and NABL accredited Test & Type Test Reports (TTR) for the offered model shall be furnished. The luminaire shall comply with relevant provisions of IS 10322.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 45.00 | Nos. |  | 3575.00 | 160875.00 | 2200.00 | 99000.00 | 1800.00 | 81000.00 | 1935.00 | 87075.00 | 81000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
7.00 | Supply of round surface mounted backlit LED downlighter with system wattage not exceeding 18W and minimum system lumen output of 2250 lumens, ensuring system luminous efficacy ≥125 lm/W.The luminaire shall be constructed from pressure die cast aluminium housing in glossy white powder coated finish, complete with high transmittivity PMMA/PC inset diffuser (deep recess type) to ensure low glare and uniform light distribution. The fixture shall be sleek in design with a maximum depth not exceeding 40 mm.The luminaire shall have CRI ≥80, SDCM ≤5, and CCT of 5700 - 6500K. The rated life shall be L70 ≥50,000 hours.Electrical parameters shall include power factor ≥0.95, THD ≤10%, suitable for an operating voltage range of 140–270 VAC, with inbuilt surge protection of minimum 4 kV.The LED driver shall have efficiency ≥85% and shall include short circuit and open circuit protection, along with P2P protection up to 440V for minimum 4 hours, and low/high voltage cutoff with auto recovery feature.The fixture shall operate within a temperature range of -10°C to +45°C and shall comply with Electrical Class I protection, IP20 ingress protection, and IK03 impact resistance.The thermal management shall be ensured through an efficient aluminium heat sink design, maintaining LED junction temperature below 90°C.The maximum power consumption shall not exceed the specified rating. The luminaire and driver shall be BIS compliant, and valid certificates shall be submitted. LM-79, LM-80, and TTR reports from NABL accredited laboratories shall also be provided.The luminaire and lighting performance shall comply with relevant provisions of IS 10322.The manufacturer’s name/logo shall be engraved/embossed/screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 125.00 | Nos. |  | 1251.00 | 156375.00 | 750.00 | 93750.00 | 700.00 | 87500.00 | 745.00 | 93125.00 | 87500.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
8.00 | Supply of round recessed mounted backlit LED downlighter having system wattage not exceeding 24W and minimum system lumen output of 3000 lumens, ensuring system luminous efficacy ≥125 lm/W.The luminaire shall be constructed from pressure die cast aluminium housing in glossy white powder coating finish, complete with high transmittivity PMMA/PC inset diffuser (deep recess type) to ensure low glare and uniform light distribution. The fixture shall be sleek in design with a maximum depth not exceeding 40 mm.The luminaire shall have CRI ≥80, SDCM ≤5, and CCT of 5700 - 6500K. The rated life shall be L70 ≥50,000 hours.Electrical parameters shall include power factor ≥0.95, THD ≤10%, suitable for an operating voltage range of 140–270 VAC, with inbuilt surge protection of minimum 4 kV.The LED driver shall have efficiency ≥85% and shall include short circuit and open circuit protection, along with P2P protection up to 440V for minimum 4 hours, and low/high voltage cutoff with auto recovery feature.The fixture shall operate within a temperature range of -10°C to +45°C and shall comply with Electrical Class I protection, IP20 ingress protection, and IK03 impact resistance.The thermal management shall be ensured through an efficient aluminium heat sink design, maintaining LED junction temperature below 90°C. The maximum power consumption shall not exceed the specified rating. The luminaire and driver shall be BIS compliant, and valid certificates shall be submitted. LM-79, LM-80, and TTR reports from NABL accredited laboratories shall also be provided.The luminaire and lighting performance shall comply with relevant provisions of IS 10322.The manufacturer’s name/logo shall be engraved/embossed/screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 170.00 | Nos. |  | 1144.00 | 194480.00 | 800.00 | 136000.00 | 1100.00 | 187000.00 | 755.00 | 128350.00 | 128350.00 | KIVASA GLOBALTECH PVT LTD
9.00 | Supplying of Street light LED fixture, Wattage ≥ 70W, powder coated pressure die cast aluminum body with built in or separate driver as per the requirement with Driver efficiency >85%, Input voltage: 140-270 Volt AC, freq 50 hz, Operating temp range -15 deg to 50 deg centigrade, internal surge protection of 5 KV L,N,E as per IEC 61000-4-5, Driver efficiency >85%,THD < 10% as per IEC 61000-3-2 , P. F.≥0.95, IP-66,IK-08, CRI >80 , under voltage and over voltage protection,EMIEMC as per CISPR-15, lenses for beam angle as per IESNA type I/II/III as per the width of the road and the project requirement., suitable to fit in up to 65mm dia pipe, life time (LED,Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report , CCT 5700 - 6500 °K (As per ANSI Bin) , SDCM(Standard Deviation Color Matching) <5, Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard complete in all respect i/c connections with 1.5 sq mm FRLS, PVC insulated copper conductor single core cable and earthing etc. as required. System lumen efficacy >125 lm/Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size i/c beam shall angle be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C).The manufacturer’s name/logo shall be engraved/embossed/screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 275.00 | Nos. |  | 2002.00 | 550550.00 | 2300.00 | 632500.00 | 1900.00 | 522500.00 | 1620.00 | 445500.00 | 445500.00 | KIVASA GLOBALTECH PVT LTD
10.00 | Supplying of Flood Canopy Light (560 x 360mm), Wattage ≥ 70W, powder coated pressure die cast aluminum body with built in or separate driver as per the requirement with Driver efficiency >85%, Input voltage: 140-270 Volt AC, freq 50 hz, Operating temp range -10 deg to 45 deg centigrade, internal surge protection of 4 KV L,N,E as per IEC 61000-4-5,THD < 10% as per IEC 61000-3-2 , P. F.≥0.95, IP-66,IK-08, CRI >70 , under voltage and over voltage protection, EMI-EMC as per CISPR-15, lenses for beam angle 30 deg- 120deg as per the application and the project requirement deg., suitable tilt able fitting, life time (LED,Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report , CCT 5700 - 6500°K (As per ANSI Bin) , SDCM(Standard Deviation Color Matching) <5, Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard complete in all respect i/c connections with 1.5 sq mm FRLS, PVC insulated copper conductor single core cable and earthing etc. as required . System lumen efficacy >135 lm/Watt output . LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size i/c beam angle shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C).The manufacturer’s name/logo shall be engraved/embossed/screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 120.00 | Nos. |  | 4290.00 | 514800.00 | 2350.00 | 282000.00 | 2000.00 | 240000.00 | 2170.00 | 260400.00 | 240000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
11.00 | Supplying of Flood Light, Wattage ≥ 50W, powder coated pressure die cast aluminum body with built in or separate driver as per the requirement with Driver efficiency >85%, Input voltage: Input voltage: 140-270 Volt AC, freq 50 hz, Operating temp range -10 deg to 45 deg centigrade, internal surge protection of 4 KV L,N,E as per IEC 61000-4-5, Driver efficiency >85%,THD < 10% as per IEC 61000-3-2 , P. F.≥0.95, IP-66,IK-08, CRI >70 , under voltage and over voltage protection, EMI-EMC as per CISPR-15, lenses for beam angle 30 deg- 120deg as per the application and the project requirement deg., suitable tilt able fitting, life time (LED,Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report , CCT 2700°K to 6500°K (As per ANSI Bin) , SDCM(Standard Deviation Color Matching) <5, Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard complete in all respect i/c connections with 1.5 sq mm FRLS, PVC insulated copper conductor single core cable and earthing etc. as required. System lumen efficacy >135 lm/Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size i/c beam angle and CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C).The manufacturer’s name/logo shall be engraved/embossed/screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 325.00 | Nos. |  | 1787.00 | 580775.00 | 1850.00 | 601250.00 | 1300.00 | 422500.00 | 1270.00 | 412750.00 | 412750.00 | KIVASA GLOBALTECH PVT LTD
12.00 | Supplying of high bay Light, Wattage ≥ 100W, powder coated pressure die cast aluminum body with built in or separate driver as per the requirement with Driver efficiency >85%, Input voltage: 140-270 Volt AC, freq 50 hz, Operating temp range -10 deg to 45 deg centigrade, internal surge protection of 4 KV L,N,E as per IEC 61000-4-5, Driver efficiency >85%,THD < 10% as per IEC 61000-3-2 , P. F.≥0.95, IP-66,IK-07, CRI >70 , under voltage and over voltage protection, EMI-EMC as per CISPR-15, lenses for beam angle 30 deg- 120deg as per the application and the project requirement deg., Suitable for suspension / hook mounting / bracket mounting as required, life time (LED,Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report , CCT 5700 - 6500°K (As per ANSI Bin) , SDCM(Standard Deviation Color Matching) <5, Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard complete in all respect i/c connections with 1.5 sq mm FRLS, PVC insulated copper conductor single core cable and earthing etc. as required. System lumen efficacy >130 lm/Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size i/c beam angle shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C).The manufacturer’s name/logo shall be engraved/embossed/screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 225.00 | Nos. |  | 3575.00 | 804375.00 | 2700.00 | 607500.00 | 3150.00 | 708750.00 | 4550.00 | 1023750.00 | 607500.00 | SYNERGY LIGHTING SOLUTIONS
13.00 | Supplying of high bay Light, Wattage ≥ 200W, powder coated pressure die cast aluminum body with built in or separate driver as per the requirement with Driver efficiency >85%, Input voltage: 140-270 Volt AC, freq 50 hz, Operating temp range -10 deg to 45 deg centigrade, internal surge protection of 5 KV L,N,E as per IEC 61000-4-5,THD < 10% as per IEC 61000-3-2 , P. F.≥0.95, IP-66,IK-07, CRI >70 , under voltage and over voltage protection, EMI-EMC as per CISPR-15, lenses for beam angle 30 deg- 120deg as per the application and the project requirement deg., Suitable for hook mounting, suspension mounting or bracket mounting as required, life time (LED,Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report , CCT 5700°K (As per ANSI Bin) , SDCM(Standard Deviation Color Matching) <5, Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard complete in all respect i/c connections with 1.5 sq mm FRLS, PVC insulated copper conductor single core cable and earthing etc. as required. System lumen efficacy >130 lm/Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size i/c beam angle shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C).The manufacturer’s name/logo shall be engraved/embossed/screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 60.00 | Nos. |  | 7150.00 | 429000.00 | 5400.00 | 324000.00 | 5265.00 | 315900.00 | 6315.00 | 378900.00 | 315900.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
14.00 | Supplying of Flood Light, Wattage ≥ 190W, powder coated pressure die cast aluminum body with built in or separate driver as per the requirement with Driver efficiency >85%, Input voltage: 140-270 Volt AC, freq 50 hz, Operating temp range -10 deg to 45 deg centigrade, internal surge protection of 5 KV L,N,E as per IEC 61000-4-5,THD < 10% as per IEC 61000-3-2 , P. F.≥0.95, IP-66,IK-07, CRI >70 , under voltage and over voltage protection, EMI-EMC as per CISPR-15, lenses for beam angle 30 deg- 120deg as per the application and the project requirement deg., suitable tilt able fitting, life time (LED,Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report , CCT 5700 - 6500°K (As per ANSI Bin) , SDCM(Standard Deviation Color Matching) <5, Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard complete in all respect i/c connections with 1.5 sq mm FRLS, PVC insulated copper conductor single core cable and earthing etc. as required. System lumen efficacy >135 lm/Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size shall i/c beam angle be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C).The manufacturer’s name/logo shall be engraved/embossed/screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 50.00 | Nos. |  | 6792.00 | 339600.00 | 5100.00 | 255000.00 | 4900.00 | 245000.00 | 3990.00 | 199500.00 | 199500.00 | KIVASA GLOBALTECH PVT LTD
15.00 | Supplying of Flood Light, Wattage ≥ 350W, powder coated pressure die cast aluminum body with built in or separate driver as per the requirement with Driver efficiency >85%, Input voltage: 140-270 Volt AC, freq 50 hz, Operating temp range -10 deg to 45 deg centigrade, internal surge protection of 5 KV L,N,E as per IEC 61000-4-5,THD < 10% as per IEC 61000-3-2 , P. F.≥0.95, IP-66,IK-07, CRI >70 , under voltage and over voltage protection, EMI-EMC as per CISPR-15, lenses for beam angle 30 deg- 120deg as per the application and the project requirement deg., suitable tilt able fitting, life time (LED,Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report , CCT 5700°K (As per ANSI Bin) , SDCM(Standard Deviation Color Matching) <5, Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard complete in all respect i/c connections with 1.5 sq mm FRLS, PVC insulated copper conductor single core cable and earthing etc. as required. System lumen efficacy >125 lm/Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size i/c beam angle shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C).The manufacturer’s name/logo shall be engraved/embossed/screen-printed on the luminaire housing.The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 150.00 | Nos. |  | 12515.00 | 1877250.00 | 7400.00 | 1110000.00 | 7700.00 | 1155000.00 | 12325.00 | 1848750.00 | 1110000.00 | SYNERGY LIGHTING SOLUTIONS
16.00 | Supply of LED Underwater Fountain Light, 18W or higher, IP68 protection, SS-316 stainless steel body, corrosion-resistant construction with toughened glass front cover, high-brightness colour-changing LEDs (RGB/RGBW), beam angle 15°–45° (as applicable), operating temperature -10°C to +50°C, IK08 or higher impact protection, LED life minimum 50,000 burning hours, surge protection minimum 2 kV, suitable for continuous underwater operation for decorative fountain and water feature illumination, operating on 12/24V AC/DC through external driver/transformer, complete with minimum 2 m waterproof cable, mounting bracket suitable for fixing on fountain nozzle ring/manifold structure i/c all necessary fittings, complete in all respects as required and approved by Engineer-in-Charge, with minimum 5-year comprehensive OEM warranty. Note: The item shall include one complete controller set, waterproof splitter/junction box, minimum 30 m control cable and all associated accessories required for operation of the complete system comprising 30 nos. of underwater fountain lights. | 35.00 | Nos. |  | 10010.00 | 350350.00 | 2500.00 | 87500.00 | 11800.00 | 413000.00 | 15500.00 | 542500.00 | 87500.00 | SYNERGY LIGHTING SOLUTIONS
17.00 | 9W LED Lamp, Wattage ≥ 9W,CCT 5700°K, Shape-B22 (Make: As per list of approved make of AAI) | 110.00 | Nos. |  | 143.00 | 15730.00 | 45.00 | 4950.00 | 50.00 | 5500.00 | 54.00 | 5940.00 | 4950.00 | SYNERGY LIGHTING SOLUTIONS
18.00 | Supply of 400mm sweep, up to 1400RPM plastic wall fan having PP material 3 nos of blade, Control Method- Pull string, Air Flow Capacity 85 cmm with minimum 2 years comprehensive warranty from OEM with all standard accessories etc., complete as required.(Make- Crompton, Model-Hiflo Wave Plus or equivalent from preferred make). | 20.00 | Nos. |  | 4004.00 | 80080.00 | 2000.00 | 40000.00 | 2400.00 | 48000.00 | 2230.00 | 44600.00 | 40000.00 | SYNERGY LIGHTING SOLUTIONS
19.00 | Supply of 400mm sweep, up to 1400RPM telescopic height adjustable metal pedestal fan made of Aluminium alloy material 3 nos of blade, Control Method- Regulator, Air Flow Capacity 100 cmm with minimum 2 years comprehensive warranty from OEM with all standard accessories etc., complete as required.(Make- Crompton , Model-Storm PF INH or equivalent from preferred make). | 20.00 | Nos. |  | 5005.00 | 100100.00 | 3000.00 | 60000.00 | 3700.00 | 74000.00 | 3300.00 | 66000.00 | 60000.00 | SYNERGY LIGHTING SOLUTIONS
20.00 | Supply of decorative outdoor LED Cylinder Bollard Light equivalent to Jaguar Model No. OBL-GRY-LBLDCYL010XW, 10W, Warm White (WW), complete with LED lamp/module, die-cast aluminium body, weatherproof construction, suitable for pathway and landscape lighting applications, complete with all accessories and fittings, having minimum IP65 protection, complete in all respects as required and approved by Engineer-in-Charge.The manufacturer’s name/logo shall be engraved/embossed/screen-printed on the luminaire housing. The luminaire shall be supplied with a minimum 5-year comprehensive warranty provided by OEM. | 47.00 | Nos. |  | 5720.00 | 268840.00 | 2900.00 | 136300.00 | 5275.00 | 247925.00 | 1530.00 | 71910.00 | 71910.00 | KIVASA GLOBALTECH PVT LTD
21.00 | Supplying of LED bulkhead light suitable for outdoor wall/ceiling mounting in building exteriors, corridors, staircases and service areas, complete in all respects. The luminaire shall be of wattage ≥18W with system luminous efficacy ≥100 lm/W, operating on 140–270V AC, 50Hz, having driver efficiency ≥85%, PF ≥0.95, THD <10%, CRI ≥80 and CCT 5700 - 6500K. The fitting shall have pressure die-cast aluminium/UV stabilized polycarbonate housing with UV stabilized diffuser, minimum IP65 ingress protection and IK08 impact resistance. The luminaire shall be provided with minimum 4kV surge protection, short circuit and open circuit protection and EMI/EMC compliance as per CISPR-15. The luminaire shall have rated life L70 ≥50,000 burning hours. The manufacturer’s name/logo shall be engraved/embossed/screen-printed on the luminaire housing. The luminaire shall be supplied with minimum 5-year comprehensive warranty provided by OEM. | 50.00 | Nos. |  | 2145.00 | 107250.00 | 700.00 | 35000.00 | 1140.00 | 57000.00 | 680.00 | 34000.00 | 34000.00 | KIVASA GLOBALTECH PVT LTD
22.00 | Supply of Desert Air Cooler having minimum 75 litre water tank capacity, suitable for cooling rooms up to 25 m² or more, fitted with heavy-duty fan, high-efficiency honeycomb cooling pads, automatic air swing, minimum three-speed operation, operating on 230 V AC, 50 Hz single-phase supply with rated power consumption not exceeding 250 W. The cooler shall have a heavy-duty UV-stabilized, rust-proof, corrosion-resistant engineering plastic body, high-efficiency motor, durable water circulation pump, four heavy-duty castor wheels, water level indicator, drain arrangement, power cord with plug top and all standard accessories. The item shall be supplied complete with delivery at site, positioning, testing, demonstration and handing over, as required. The complete unit shall be backed by a minimum 2 (Two) years comprehensive on-site OEM warranty. | 10.00 | Nos. |  | 15730.00 | 157300.00 | 3000.00 | 30000.00 | 15910.00 | 159100.00 | 8600.00 | 86000.00 | 30000.00 | SYNERGY LIGHTING SOLUTIONS
23.00 | Supply, Installation, Testing & Commissioning (SITC) of large Stretch ceiling luminaire having dimensions as per approved drawings/site requirements & Wattage of 40W/SqMtr, fixture to be made up of Aluminium extruded in Powder Coated white finish having curved shaped opposite corners. fixture to be with White Translucent Stretchable PVC diffuser with acoustic propertise & to be certified b-s1-d0/b-s2-d0 in acc. with DIN EN 13501 which indicates low inflammability, limited development of smoke and no combustible drips. The stretchable diffuser should be RoHS directive compliance, Certified low heavy metal migration, Certified low water vapour permeability & Certified low emissions, class A+. The LED source to be from Nichia or Osram or equivalent from AAI approved/preferred makes & Double track Aluminium PCB must be used for better heat dissipation with double coating - 20 μ Copper plated light. LED Efficacy to be min 100lm/W with CRI>90, SCDM ≤ 3. Each LED to have optical PMMA - Aspheric Design Lens used for bat wing wide beam angle > 170. The CCT should be 6500k. The CRI of the luminiare should be not less than 90, SCDM ≤ 3, each LED to be with Optical PMMA - Aspheric Design Lens used for even distribution. The luminaire should have a life of 50,000 burning hours (L70). The luminaire should have acoustics properties of αw 0.6 class C EN 11654. The luminaire driver should be IP33 & voltage range to be 140 to 277 VAC, PF 0.95. The lumnaire should be compatible for ambient temp of 5 to 35 °C.The fabric shall have fire rating B-s1,d0 and the panel shall have fire rating B-s2,d0 as per EN 13501. Fixture to be completed in all respect similar to Bajaj Fluence Stretch ceiling luminaire or equivalent from AAI approved/preferred makes.The item shall include complete aluminium extruded supporting frame, stretch PVC diffuser, LED modules, LED driver, suspension arrangement, trap doors wherever required for maintenance, fixing accessories, internal wiring, interconnections, testing, commissioning and all other materials, labour, tools, tackles and accessories required for complete installation and satisfactory operation, complete in all respects. The complete luminaire, including LED modules, LED driver, stretch PVC diffuser and all associated components, shall be covered under a minimum 5 (Five) years comprehensive OEM warranty from the date of successful commissioning. During the warranty period, any defective component shall be repaired or replaced by the contractor/OEM within prescribed time limit at no extra cost to AAI as per tender conditions. | 200.00 | Sqmtr |  | 5720.00 | 1144000.00 | 16750.00 | 3350000.00 | 18000.00 | 3600000.00 | 11350.00 | 2270000.00 | 1144000.00 | Instapower Ltd
24.00 | SH-II, ITC of LED Fittings Installation, testing and commissioning of LED panel luminaires of sizes 2' × 2' and 1' × 4' in Gypsum ceiling/ Drop-ceiling/ suspended ceiling/ T-bar ceilinng of office buildings / airport buildings / ancillary buildings, at height up to 5.0 meters, including replacement of existing fittings, dismantling of old fittings and stacking/shifting the same in AAI store room, installation at new locations including cutting/making openings in false ceiling, alteration/modification of existing cut-outs, fixing, alignment, providing support clamp/ metal chain , providing electrical connections(i/c connections with 1.5 sq mm FRLS, PVC insulated copper conductor single core cable and earthing etc.) with existing wiring, earthing, testing and commissioning, complete, as per directions of Engineer-in-Charge. | 526.00 | Nos. |  | 250.00 | 131500.00 | 45.00 | 23670.00 | 150.00 | 78900.00 | 200.00 | 105200.00 | 23670.00 | SYNERGY LIGHTING SOLUTIONS
25.00 | Installation, testing and commissioning of LED surface-mounted batten lights of 20 W and 40 W in offices / airport buildings / ancillary buildings, at height up to 5.0 metre, including replacement of existing batten fittings, dismantling of old fittings and stacking/shifting the same in AAI store room, installation at new locations, fixing on wall/ceiling including making holes, anchors and supports as required, electrical connections(i/c connections with 1.5 sq mm FRLS, PVC insulated copper conductor single core cable and earthing etc.) , earthing, testing and commissioning, complete, as per directions of Engineer-in-Charge. | 718.00 | Nos. |  | 300.00 | 215400.00 | 20.00 | 14360.00 | 150.00 | 107700.00 | 200.00 | 143600.00 | 14360.00 | SYNERGY LIGHTING SOLUTIONS
26.00 | Installation, testing and commissioning of non-flammable LED batten lights in offices / airport buildings / ancillary buildings, at height up to 4.0 metre, including replacement of existing fittings, dismantling of old fittings and stacking/shifting the same in AAI store room, installation at new locations, fixing on wall/ceiling including drilling, anchors, clamps and supports as required, electrical connections, earthing, testing and commissioning, complete, as per directions of the Engineer-in-Charge. | 12.00 | Nos. |  | 400.00 | 4800.00 | 20.00 | 240.00 | 150.00 | 1800.00 | 200.00 | 2400.00 | 240.00 | SYNERGY LIGHTING SOLUTIONS
27.00 | Installation, testing and commissioning of terminal building city-side canopy edge LED lights at airport city-side buildings / terminal canopies, at height up to 7.0 metres, including replacement of existing fittings, dismantling of old canopy lights and stacking/shifting the same in AAI store room, installation at new or existing locations, fixing of luminaires using long metal pipe (MS/GI) mounting arrangement, including cutting, fabrication, welding and fixing of suitable pipe, brackets, clamps and support mechanism on existing canopy structure, proper alignment and leveling of fittings, electrical connections through the pipe, earthing, testing and commissioning, complete, as per directions of the Engineer-in-Charge. | 40.00 | Nos. |  | 1000.00 | 40000.00 | 100.00 | 4000.00 | 200.00 | 8000.00 | 250.00 | 10000.00 | 4000.00 | SYNERGY LIGHTING SOLUTIONS
28.00 | Installation, testing and commissioning of LED surface-mounted round downlighters in offices / airport buildings / ancillary buildings, at height up to 5.0 metres, including replacement of existing surface-mounted fittings, dismantling of old fittings and stacking/shifting the same in AAI store room, installation at new locations on ceiling/wall surface, fixing with suitable clamps, anchors, screws and mounting accessories, routing/termination of wiring through surface conduit wherever required, electrical connections, earthing, testing and commissioning, complete, as per directions of the Engineer-in-Charge. | 106.00 | Nos. |  | 800.00 | 84800.00 | 30.00 | 3180.00 | 175.00 | 18550.00 | 200.00 | 21200.00 | 3180.00 | SYNERGY LIGHTING SOLUTIONS
29.00 | Installation, testing and commissioning of LED recessed round downlighters in false ceiling of offices / airport buildings / ancillary buildings, at height up to 4.0 metres, including replacement of existing recessed downlighters, dismantling of old fittings and stacking/shifting the same in AAI store room, installation at new locations, cutting/making fresh circular openings in false ceiling of suitable size, modification/enlargement of existing cut-outs wherever required, proper fixing of fittings using spring clips / mounting mechanism, electrical connections, earthing, testing and commissioning, complete, as per directions of the Engineer-in-Charge. | 139.00 | Nos. |  | 800.00 | 111200.00 | 30.00 | 4170.00 | 175.00 | 24325.00 | 200.00 | 27800.00 | 4170.00 | SYNERGY LIGHTING SOLUTIONS
30.00 | Installation, testing and commissioning of LED street light luminaires of 70 W at roads, parking areas, peripheral roads, service roads and other outdoor areas of airport / ancillary buildings, height up to 12.0 metres as per site requirement, including replacement of existing street light fittings, dismantling of old luminaires and stacking/shifting the same in AAI store room, installation at new locations, mounting on existing or new pole arms (up to 65 mm dia), fixing and alignment of luminaires, electrical connections from pole junction box using existing/new cables, earthing, testing and commissioning, complete, as per directions of the Engineer-in-Charge. | 260.00 | Nos. |  | 1000.00 | 260000.00 | 100.00 | 26000.00 | 250.00 | 65000.00 | 250.00 | 65000.00 | 26000.00 | SYNERGY LIGHTING SOLUTIONS
31.00 | Installation, testing and commissioning of LED flood / canopy down-lights, fixed below the terminal building canopy (underside mounting) for airport entry, drop-off and pedestrian covered areas, at height up to 9.0 metres, including replacement of existing underside canopy lights, dismantling of old fittings and stacking/shifting the same in AAI store room, installation at new locations below canopy, fabrication, welding, cutting and fixing of suitable mounting brackets / frames / hangers / supports for underside canopy fixing, proper alignment and tilting to achieve downward illumination, electrical connections, earthing, testing and commissioning, complete, as per directions of the Engineer-in-Charge. | 116.00 | Nos. |  | 1000.00 | 116000.00 | 100.00 | 11600.00 | 250.00 | 29000.00 | 250.00 | 29000.00 | 11600.00 | SYNERGY LIGHTING SOLUTIONS
32.00 | Installation, testing and commissioning of LED flood lights having system wattage not less than 50 W at airport buildings, facades, landscape areas, boundary areas, canopies or other outdoor locations, at height up to 9.0 metres (or as per site requirement), including replacement of existing flood lights, dismantling of old fittings and stacking/shifting the same in AAI store room, installation at new locations, fixing on wall / structure / canopy / pole / pedestal as applicable, including cutting, fabrication, drilling, anchoring and fixing of suitable mounting brackets, clamps or supports, proper tilting and alignment to achieve required beam direction, electrical connections, earthing, testing and commissioning, complete, as per directions of the Engineer-in-Charge. | 316.00 | Nos. |  | 1000.00 | 316000.00 | 100.00 | 31600.00 | 250.00 | 79000.00 | 250.00 | 79000.00 | 31600.00 | SYNERGY LIGHTING SOLUTIONS
33.00 | Installation, testing and commissioning of LED high-bay / flood light luminaires of 100W / 190 W/ 200W, at terminal buildings, hangars, cargo buildings, covered halls, yards, aprons, peripheral areas and other indoor/outdoor locations of airport / ancillary buildings, at height up to 22.0 metres (or as per site requirement), including replacement of existing high-bay / flood light fittings, dismantling of old luminaires and stacking/shifting the same in AAI store room, installation at new locations, fixing on ceiling / beam / truss / wall / pole / structure as applicable, including cutting, fabrication, welding, drilling, anchoring and fixing of suitable mounting brackets, frames, clamps or supports, proper tilting, aiming and alignment of luminaires, electrical connections, earthing, testing and commissioning, complete, as per directions of the Engineer-in-Charge. | 305.00 | Nos. |  | 1500.00 | 457500.00 | 200.00 | 61000.00 | 350.00 | 106750.00 | 250.00 | 76250.00 | 61000.00 | SYNERGY LIGHTING SOLUTIONS
34.00 | Installation, testing and commissioning of LED flood light luminaires of 350W at terminal buildings, hangars, cargo buildings, covered halls, yards, aprons, peripheral areas and other indoor/outdoor locations of airport / ancillary buildings, at height up to 16.0 metres (or as per site requirement), including replacement of existing high-bay / flood light fittings, dismantling of old luminaires and stacking/shifting the same in AAI store room, installation at new locations, fixing on ceiling / beam / truss / wall / pole / structure as applicable, including cutting, fabrication, welding, drilling, anchoring and fixing of suitable mounting brackets, frames, clamps or supports, proper tilting, aiming and alignment of luminaires, electrical connections, earthing, testing and commissioning, complete, as per directions of the Engineer-in-Charge. | 136.00 | Nos. |  | 1000.00 | 136000.00 | 100.00 | 13600.00 | 300.00 | 40800.00 | 250.00 | 34000.00 | 13600.00 | SYNERGY LIGHTING SOLUTIONS
35.00 | Installation, testing and commissioning of garden fountain coloured LED flood lights of 18W at airport gardens, landscape areas, fountains and other outdoor decorative locations, including replacement of existing fountain/landscape lights, dismantling of old fittings and stacking/shifting the same in AAI store room, installation at new locations, fixing on ground / pedestal / structure / fountain edge or underwater mounting arrangement as applicable, including cutting, drilling, anchoring and fixing of suitable mounting brackets/supports, waterproof electrical connections with suitable glands, joints and sealing, earthing, testing and commissioning, complete, as per directions of the Engineer-in-Charge. | 30.00 | Nos. |  | 2000.00 | 60000.00 | 100.00 | 3000.00 | 175.00 | 5250.00 | 250.00 | 7500.00 | 3000.00 | SYNERGY LIGHTING SOLUTIONS
36.00 | Installation, testing and commissioning of decorative LED bollard lights of 10W along pedestrian footpath through garden area in front of terminal building, including fixing of bollard on RCC pedestal / foundation with anchor bolts, routing and termination of underground cable, electrical connections, earthing, testing and commissioning, complete, as per directions of the Engineer-in-Charge. | 47.00 | Nos. |  | 1500.00 | 70500.00 | 200.00 | 9400.00 | 2000.00 | 94000.00 | 3500.00 | 164500.00 | 9400.00 | SYNERGY LIGHTING SOLUTIONS
37.00 | Installation, testing and commissioning of LED bulkhead lights of 18W on wall / ceiling / trench wall / service corridor / outdoor building surface, including replacement of existing fittings at height up to 4.0 metres, dismantling of old fittings and stacking/shifting the same in AAI store room, fixing of new bulkhead light with suitable screws, anchors and mounting accessories, electrical connections, earthing, testing and commissioning, complete, as per directions of the Engineer-in-Charge. | 37.00 | Nos. |  | 400.00 | 14800.00 | 30.00 | 1110.00 | 75.00 | 2775.00 | 250.00 | 9250.00 | 1110.00 | SYNERGY LIGHTING SOLUTIONS
| Total in Figures |  |  |  |  | 12120176.25 |  | 9351930.00 |  | 10617425.00 |  | 9890075.00
Lowest Amount Quoted BY: SYNERGY LIGHTING SOLUTIONS(9351930.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of New LED light fittings and associated Electrical Works at Vadodara Airport Tender ID: 2026_AAI_285496_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SYNERGY LIGHTING SOLUTIONS (BID ID -1063066) | 9351930.00 | L1
| 2 | KIVASA GLOBALTECH PVT LTD (BID ID -1052461) | 9890075.00 | L2
| 3 | Krishsons International Engineers And Consultants (I) Pvt. Ltd (BID ID -1062658) | 10617425.00 | L3
| 4 | Instapower Ltd (BID ID -1056312) | 12120176.25 | L4