## BoQ1
Government eProcurement System Created By: A NARASIMHA PRASAD Created Date/Time: 07-Sep-2026 04:08 PM Tender Title: Renovation of Electrical Works and its Allied Works at MT Section RHQ SR Chennai Airport Tender ID: 2026_AAI_286551_1
Tender Inviting Authority: SENIOR MANAGER (ENGG-ELECTRICAL), AAI, RHQ-SR, CHENNAI - 600016
Name of Work: Renovation of Electrical Works and its Allied Works at MT Section RHQ-SR, Chennai Airport.
Contract No: 2026_AAI_286551_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CHENNAI ENGINEERING SERVICES (GSTN-33AADFC4373K1ZH) BID ID -1062044 |  | Balaji Engineering (GSTN-33ADGPV2628A1ZV) BID ID -1063827 |  | vk sam engineering (GSTN-33AMZPS4037L1ZA) BID ID -1063918 |  | Limra Electricals (GSTN-33CIVPS8740L1ZA) BID ID -1064003 |  | DEEPAKELECTRICALS (GSTN-33ALUPD3531C1ZI) BID ID -1064029 |  | DElite System Engineering (India) Pvt. Ltd. (GSTN-NA) BID ID -1062424
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH- I: Supply of LED Lighting fixtures
1.01 | Supply of suspended type Industrial LED High Bay Luminaire comprising high-efficiency LED module, pressure die-cast aluminium housing with integral heat sink, constant current electronic LED driver, high-transmittance UV-stabilized polycarbonate optical lens, complete with suspension hook/chain, mounting accessories and all necessary hardware. The luminaire shall have a system wattage of 70 W, minimum system lumen output of 10000 lumens, minimum luminaire efficacy of 110 lm/W, correlated colour temperature (CCT) between 5700 K and 6500 K, CRI ≥ 80, power factor ≥ 0.95, THD ≤ 10%, surge protection ≥ 4 kV, IP65 protection, impact resistance IK08, L70 life ≥ 50,000 hours, suitable for 230 V, 50 Hz AC supply and outdoor/industrial applications, complete as per the technical specifications. (Similar to Bajaj CAT No. OPTIBAY 80W WH NB PC SD or approved equivalent.) | 30.00 | Each |  | 11569.00 | 347070.00 | 5000.00 | 150000.00 | 4099.00 | 122970.00 | 4550.00 | 136500.00 | 12000.00 | 360000.00 | 5099.00 | 152970.00 | 122970.00 | vk sam engineering
1.02 | Supply of LED Street Light Luminaire complete with high-efficiency LED module, pressure die-cast aluminium housing with integral heat sink, UV-stabilized polycarbonate optical lens, constant current electronic LED driver, and all mounting accessories. The luminaire shall have a rated system wattage of approximately 45 W, minimum system lumen output of 4,950 lumens, minimum luminaire efficacy of 130 lm/W, correlated colour temperature (CCT) between 5700 K and 6500 K, CRI ≥ 70, power factor ≥ 0.95, THD ≤ 10%, surge protection ≥ 4 kV, ingress protection IP66, impact resistance IK08, L70 life ≥ 50,000 hours, suitable for operation on 230 V, 50 Hz AC supply for outdoor applications, complete with all fixing accessories and conforming to the technical specifications. Similar to Bajaj Cat. No. ENXT P 54L WH PO PC SD or approved equivalent. | 15.00 | Each |  | 4159.00 | 62385.00 | 4500.00 | 67500.00 | 1840.00 | 27600.00 | 3450.00 | 51750.00 | 5500.00 | 82500.00 | 2099.00 | 31485.00 | 27600.00 | vk sam engineering
1.03 | Supply of surface/suspended batten LED luminaire of nominal length 1200 mm comprising CRCA sheet steel/extruded aluminium housing with silver powder-coated finish, high-transmittance UV-stabilized opal diffuser made of Polycarbonate (PC), high-efficiency LED module and constant current electronic LED driver, complete with all fixing accessories. The luminaire shall have a minimum system lumen output of 4,000 lumens, minimum luminaire efficacy of 100 lm/W, correlated colour temperature (CCT) between 5700 K and 6500 K, CRI ≥ 80, power factor ≥ 0.95, THD ≤ 10%, L70 life ≥ 50,000 hours, suitable for operation on 230 V, 50 Hz AC supply for indoor applications, complete as per technical specifications. (Similar to Havells Cat. No. Elenor LED Broad Batten 40 W 6500 K or approved equivalent.) | 45.00 | Each |  | 919.00 | 41355.00 | 2000.00 | 90000.00 | 635.00 | 28575.00 | 1950.00 | 87750.00 | 1400.00 | 63000.00 | 599.00 | 26955.00 | 26955.00 | DElite System Engineering (India) Pvt. Ltd.
1.04 | Supply of surface/suspended batten LED luminaire of nominal length 600 mm comprising CRCA sheet steel/extruded aluminium housing with silver powder-coated finish, high-transmittance UV-stabilized opal Polycarbonate (PC) or PMMA diffuser, high-efficiency LED module and constant current electronic LED driver, complete with all fixing accessories. The luminaire shall have a minimum system lumen output of 2,000 lumens, minimum luminaire efficacy of 100 lm/W, correlated colour temperature (CCT) between 5700 K and 6500 K, CRI ≥ 80, power factor ≥ 0.95, THD ≤ 10%, L70 life ≥ 50,000 hours, suitable for operation on 230 V, 50 Hz AC supply for indoor applications, complete as per the technical specifications and as directed by the Engineer-in-Charge. (Similar to approved makes such as Havells Cat No. Elenor Plus LED Broad Batten 20 W or approved equivalent.) | 20.00 | Each |  | 1189.00 | 23780.00 | 3500.00 | 70000.00 | 631.00 | 12620.00 | 1250.00 | 25000.00 | 1200.00 | 24000.00 | 599.00 | 11980.00 | 11980.00 | DElite System Engineering (India) Pvt. Ltd.
1.05 | Supply of recessed LED panel luminaire of nominal size 600 mm × 600 mm comprising CRCA sheet steel housing with white powder-coated finish, high-transmittance UV-stabilized opal Polycarbonate (PC) diffuser, high-efficiency LED module, constant current electronic LED driver, and all necessary fixing accessories. The luminaire shall have a minimum system lumen output of 3,600 lumens, minimum luminaire efficacy of 120 lm/W, correlated colour temperature (CCT) between 5700 K and 6500 K, colour rendering index (CRI) ≥ 80, power factor ≥ 0.95, THD ≤ 10%, L70 life ≥ 50,000 hours, suitable for operation on 230 V, 50 Hz AC supply for indoor applications, complete as per the technical specifications and as directed by the Engineer-in-Charge. | 5.00 | Each |  | 1269.00 | 6345.00 | 3000.00 | 15000.00 | 1921.00 | 9605.00 | 2550.00 | 12750.00 | 3000.00 | 15000.00 | 2099.00 | 10495.00 | 6345.00 | CHENNAI ENGINEERING SERVICES
1.06 | Installation, testing and commissioning of pre-wired, LED fitting of all types, complete with all accessories on false ceiling, including supports for fittings and connections with 2.5/1.5 sq. mm FRLSH PVC insulated, copper conductor, single core cable and earthing etc. as required. | 100.00 | Each |  | 249.00 | 24900.00 | 1000.00 | 100000.00 | 267.00 | 26700.00 | 50.00 | 5000.00 | 120.00 | 12000.00 | 99.00 | 9900.00 | 5000.00 | Limra Electricals
1.07 | Installation, testing and commissioning of pre-wired, Street light LED fitting of all types, complete with all accessories including suitable GI arm supports and connections with 2.5/1.5 sq. mm FRLSH PVC insulated, copper conductor, single core cable and earthing etc. as required. | 15.00 | Each |  | 659.00 | 9885.00 | 1000.00 | 15000.00 | 1067.00 | 16005.00 | 50.00 | 750.00 | 150.00 | 2250.00 | 1599.00 | 23985.00 | 750.00 | Limra Electricals
2.00 | SH- II: SITC of Fans, Air circulators and Exhaust fans
2.01 | Supply and fixing of 600mm sweep, metallic Air circulator of wall mounted type with minimum 1440 RPM and minimum Air delivery of 250 CMM and having minimum noise level 60-65 db suitable for 230 Volt 50 Hz AC Supply including all acessories etc. as required. (Make: Almonard, Havells/Crompton/Bajaj or equivalent) | 12.00 | Each |  | 8959.00 | 107508.00 | 9000.00 | 108000.00 | 7518.00 | 90216.00 | 10150.00 | 121800.00 | 9900.00 | 118800.00 | 9000.00 | 108000.00 | 90216.00 | vk sam engineering
2.02 | Supply of 1200 mm sweep BLDC Ceiling fan, BEE 5 star rated with double ball bearing, standard down rod and other standard accessories with remote etc., as required. | 16.00 | Each |  | 3339.00 | 53424.00 | 4500.00 | 72000.00 | 3026.00 | 48416.00 | 3350.00 | 53600.00 | 5500.00 | 88000.00 | 3099.00 | 49584.00 | 48416.00 | vk sam engineering
2.03 | Supply and Fixing of 450 mm sweep 230V, 50 Hz, Single Phase , 1400 rpm wall mounting fan having MS ribs guard for protection, pull cord control for speed & oscillation on off and making the electrical connections with all accessories as required. | 5.00 | Each |  | 3739.00 | 18695.00 | 3500.00 | 17500.00 | 8003.00 | 40015.00 | 4550.00 | 22750.00 | 4500.00 | 22500.00 | 5299.00 | 26495.00 | 17500.00 | Balaji Engineering
2.04 | Supply of 300mm sweep 1400 rpm heavy duty exhaust fan suitable for 230V, 50 Hz AC supply complete with motor, capacitors, and all accessories including Louver and shutter / Wire mesh Guard etc. complete as required. | 3.00 | Each |  | 2689.00 | 8067.00 | 3500.00 | 10500.00 | 2878.00 | 8634.00 | 4050.00 | 12150.00 | 4000.00 | 12000.00 | 3399.00 | 10197.00 | 8067.00 | CHENNAI ENGINEERING SERVICES
2.05 | Supply of 450mm sweep 1400 rpm heavy duty exhaust fan suitable for 230V, 50 Hz AC supply complete with motor, capacitors, and all accessories including Louver and shutter / Wire mesh Guard etc. complete as required. | 1.00 | Each |  | 4179.00 | 4179.00 | 5000.00 | 5000.00 | 4967.00 | 4967.00 | 3500.00 | 3500.00 | 5500.00 | 5500.00 | 4399.00 | 4399.00 | 3500.00 | Limra Electricals
2.06 | Installation, testing and commissioning of ceiling fan, including wiring the downrods of length (upto 60 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc., complete as required. | 16.00 | Each |  | 259.00 | 4144.00 | 500.00 | 8000.00 | 243.00 | 3888.00 | 100.00 | 1600.00 | 120.00 | 1920.00 | 200.00 | 3200.00 | 1600.00 | Limra Electricals
2.07 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. Upto 450 mm sweep | 4.00 | Each |  | 509.00 | 2036.00 | 500.00 | 2000.00 | 388.00 | 1552.00 | 100.00 | 400.00 | 500.00 | 2000.00 | 300.00 | 1200.00 | 400.00 | Limra Electricals
3.00 | SH- III: SITC of LT Panel
3.01 | Design, Fabrication and supply of PTTA cubical type LT Panel suitable for 415 V, 3 Phase, 4 wire 50 Hz AC supply, made out of 2 mm thick CRCA sheet steel/GI Sheet for frame work, doors and covers, 3 mm thick for gland plates, dust tight, vermin proof, totally enclosed, floor mounting, free standing, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 400 Amps capacity FP Aluminium bus bars of high conductivity, DMC/SMC bus bar supports with short circuit withstand capacity of 36 KA for 1 Sec., bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, panel shall have a common copper earth bar of size 50 mm x 5 mm at the rear with 2 nos. earth stud, suitable size cable termination box on both side of panel for termination of LT cables, provision of suitable size Aluminium bus bars for termination of cables, solid connections from main bus bars to switchgears with required size Aluminium bus bars and control wiring with 2.5 Sq.mm. FRLS PVC insulated copper conductor cable, cable gland plates suitable for indoor operation, complete with all accessories, connection, interconnection, earthing, alignment with the bus ducts etc., as required and comprising of following switch gears:
3.02 | Incomer: Two Nos. 250 A, 36KA, Four Pole MCCB (Ics=Icu) as Incomer with inbuilt O/L, S/C and E/F Protection with microprocessor based releases and provided with separate suitable rated three nos.Cast Resin CTs with Digital Multifunction Meter (EM6400NG of Schneider make or equivalent having RS 485 port), LED Phase Indication Lamps along with 2 Amps control MCBs as backup protection, Breaker ON/ OFF/ TRIP LED indicating lights along with control MCBs as per standard practice, Mechanical and Electrical Interlocking arrangement between the incomers & bus coupler along with interlocking relays, mechanical lock & keys etc., i/c Control MCBs, control terminals & wirings etc., as required.
3.03 | Six Nos. 125 A, 36 KA, Four Pole MCCB (Ics=Icu) as Outgoing with inbuilt O/L, S/C and E/F Protection with microprocessor based release and provided with suitable rating Cast resin CTs with digital Multifunction Meter (EM6400NG of Schneider make or equivalent) having RS 485 port, ON/ OFF/ TRIP LED indication lamp along with control MCBs as per Standard practice etc., as required.
3.04 | Six Nos. 63 A, 18 KA, Four Pole MCCB (Ics=Icu) as Outgoing with inbuilt O/L, S/C and earth fault Protection with microprocessor based release and provided with suitable rating Cast resin CTs with digital Multifunction Meter (EM6400NG of Schneider make or equivalent) having RS 485 port, ON/ OFF/ TRIP LED indication lamp along with control MCBs as per Standard practice etc., as required.
3.05 | Two Nos. 32 A, 18KA, Four Pole MCCB (Ics=Icu) as Outgoing with inbuilt O/L, S/C and earth fault Protection with microprocessor based release and provided with suitable rating Cast resin CTs with digital Multifunction Meter (EM6400NG of Schneider make or equivalent) having RS 485 port, ON/ OFF/ TRIP LED indication lamp along with control MCBs as per Standard practice etc., as required.
3.06 | Bus Coupler: One No. 250 A, 36KA, Four Pole MCCB (Ics=Icu) as Bus coupler with inbuilt O/L, S/C and earth fault Protection with microprocessor based releases, Breaker ON/OFF/Trip LED indicating lamps along with control MCBs as per standard practice including providing and fixing of suitable size Adopter Chamber in the first part to attach with the second part etc., as required.
3.07 | Bus Bar: One Set of FP Aluminium Bus Bars of minimum of 400A Capacity with heat shrinkable coloured epoxy sleeves and i/c providing and fixing of DMC/SMC bus bar supports meeting fault level of 36 KA for 1 Sec with adequate size Aluminium busbars for interconnection of incomer and outgoing switchgears etc., as required.
3.08 | Interlocking: Electrical interlocking (incommer & Bus coupler) and mechanical interlocking should be to ensure that only one supply is available at a time on each section of bus and to eliminate any possibility of accidently approaching two supply at one bus section.
3.09 | All accessories such as Extended Rotary Handle, fuses, MCBs, auxiliary contactors, auxiliary switches, ROMs for MCCBs, Phase Barriers, Phase Spreaders etc., as required.
3.10 | All Items as mentioned above under Sl. No. 3.01 to 3.08 | 1.00 | Job |  | 1049999.00 | 1049999.00 | 700000.00 | 700000.00 | 1595941.00 | 1595941.00 | 1350000.00 | 1350000.00 | 1229321.00 | 1229321.00 | 1579000.00 | 1579000.00 | 700000.00 | Balaji Engineering
3.11 | Installation, Testing and Commissioning of 415V, 250 Amps Bus bar rating, LT Panel mentioned at SH-III/Item No. 3.01-3.09 including provision of suitable mounting arrangement, assembling of LT panel, connection, interconnection, earthing, performing site acceptance test etc. complete as required. | 1.00 | Job |  | 39099.00 | 39099.00 | 10000.00 | 10000.00 | 11640.00 | 11640.00 | 25000.00 | 25000.00 | 5000.00 | 5000.00 | 5000.00 | 5000.00 | 5000.00 | DElite System Engineering (India) Pvt. Ltd., DEEPAKELECTRICALS
4.00 | SH- IV: Supply of LT Cable, cable laying & End terminations etc.,
4.01 | Supply of XLPE insulated and PVC sheathed aluminum conductor armoured power cable of 1.1 KV grade conforming to IS 7098 (Part-I) 1988 as amended upto date and of following size as required:
4.02 | 4 X 25 Sq.mm | 200.00 | Mtr |  | 259.00 | 51800.00 | 300.00 | 60000.00 | 236.00 | 47200.00 | 292.00 | 58400.00 | 270.00 | 54000.00 | 209.00 | 41800.00 | 41800.00 | DElite System Engineering (India) Pvt. Ltd.
4.03 | 4 X 35 Sq.mm | 300.00 | Mtr |  | 359.00 | 107700.00 | 350.00 | 105000.00 | 318.00 | 95400.00 | 400.00 | 120000.00 | 390.00 | 117000.00 | 299.00 | 89700.00 | 89700.00 | DElite System Engineering (India) Pvt. Ltd.
4.04 | 3.5 X 50 Sq.mm | 50.00 | Mtr |  | 409.00 | 20450.00 | 550.00 | 27500.00 | 321.00 | 16050.00 | 470.00 | 23500.00 | 550.00 | 27500.00 | 429.00 | 21450.00 | 16050.00 | vk sam engineering
4.05 | 3.5 X 95 Sq.mm | 300.00 | Mtr |  | 699.00 | 209700.00 | 1000.00 | 300000.00 | 377.00 | 113100.00 | 807.00 | 242100.00 | 750.00 | 225000.00 | 609.00 | 182700.00 | 113100.00 | vk sam engineering
4.06 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
4.07 | Upto 35 sq. mm | 50.00 | Mtr |  | 29.00 | 1450.00 | 50.00 | 2500.00 | 53.00 | 2650.00 | 50.00 | 2500.00 | 22.00 | 1100.00 | 19.00 | 950.00 | 950.00 | DElite System Engineering (India) Pvt. Ltd.
4.08 | Above 35 sq. mm and upto 95 sq. mm | 172.00 | Mtr |  | 59.00 | 10148.00 | 50.00 | 8600.00 | 63.00 | 10836.00 | 70.00 | 12040.00 | 27.00 | 4644.00 | 19.00 | 3268.00 | 3268.00 | DElite System Engineering (India) Pvt. Ltd.
4.09 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
4.10 | Upto 35 sq. mm | 50.00 | Mtr |  | 39.00 | 1950.00 | 50.00 | 2500.00 | 53.00 | 2650.00 | 50.00 | 2500.00 | 22.00 | 1100.00 | 19.00 | 950.00 | 950.00 | DElite System Engineering (India) Pvt. Ltd.
4.11 | Above 35 sq. mm and upto 95 sq. mm | 30.00 | Mtr |  | 49.00 | 1470.00 | 50.00 | 1500.00 | 63.00 | 1890.00 | 80.00 | 2400.00 | 27.00 | 810.00 | 19.00 | 570.00 | 570.00 | DElite System Engineering (India) Pvt. Ltd.
4.12 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
4.13 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 500.00 | Mtr |  | 79.00 | 39500.00 | 50.00 | 25000.00 | 63.00 | 31500.00 | 70.00 | 35000.00 | 35.00 | 17500.00 | 19.00 | 9500.00 | 9500.00 | DElite System Engineering (India) Pvt. Ltd.
4.14 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 95.00 | Mtr |  | 149.00 | 14155.00 | 50.00 | 4750.00 | 82.00 | 7790.00 | 100.00 | 9500.00 | 45.00 | 4275.00 | 19.00 | 1805.00 | 1805.00 | DElite System Engineering (India) Pvt. Ltd.
4.15 | Supplying and making end termination with brass double compression gland and Aluminium lugs for following size PVC insulated and PVC sheathed / XLPE Aluminium conductor cable of 1.1 KV grade as required.
4.16 | 4 X 25 Sq.mm | 10.00 | Each |  | 269.00 | 2690.00 | 500.00 | 5000.00 | 243.00 | 2430.00 | 200.00 | 2000.00 | 300.00 | 3000.00 | 699.00 | 6990.00 | 2000.00 | Limra Electricals
4.17 | 4 X 35 Sq.mm | 8.00 | Each |  | 299.00 | 2392.00 | 500.00 | 4000.00 | 388.00 | 3104.00 | 250.00 | 2000.00 | 350.00 | 2800.00 | 699.00 | 5592.00 | 2000.00 | Limra Electricals
4.18 | 3.5 X 50 Sq.mm | 4.00 | Each |  | 439.00 | 1756.00 | 700.00 | 2800.00 | 485.00 | 1940.00 | 350.00 | 1400.00 | 450.00 | 1800.00 | 699.00 | 2796.00 | 1400.00 | Limra Electricals
4.19 | 3.5 X 95 Sq.mm | 4.00 | Each |  | 639.00 | 2556.00 | 800.00 | 3200.00 | 534.00 | 2136.00 | 450.00 | 1800.00 | 500.00 | 2000.00 | 699.00 | 2796.00 | 1800.00 | Limra Electricals
4.20 | Supplying and laying of "B" Class G.I pipe of 65 mm dia, i/c excavation of bituminous/concrete road/pavement, excavation of trench of required width for laying of hume pipe, depth upto 800 mm, providing and laying cement concrete of 1:4:8 ratio at bottom (100 mm) of pipe, refillingthe trench with soil, ramming, watering, consolidation and making the surface to original finish with PCC of 1:2:4 ratio on top (200 mm) and disposal of left out soil away from Airport premises etc., complete as required. | 24.00 | Mtr |  | 1209.00 | 29016.00 | 1200.00 | 28800.00 | 1310.00 | 31440.00 | 1000.00 | 24000.00 | 1100.00 | 26400.00 | 1999.00 | 47976.00 | 24000.00 | Limra Electricals
4.21 | Supply and Fixing of pre-cast RCC manhole chamber of size 1000 mm X 1000 mm X 600 mm deep with wall thickness of 100 mm along with suitable RCC slab cover having 100 mm thickness with lifting hooks making as per site requirements including providing PCC base of grade 1:3:6 of 100 mm thickness at the bottom, required excavation, refilling, ramming etc., complete as required. | 2.00 | Job |  | 9179.00 | 18358.00 | 10000.00 | 20000.00 | 15365.00 | 30730.00 | 10000.00 | 20000.00 | 40000.00 | 80000.00 | 19000.00 | 38000.00 | 18358.00 | CHENNAI ENGINEERING SERVICES
5.00 | SH-V : SITC of Air-Conditioning units and Water Filter
5.01 | Supply, Installation, Testing and Commissioning of 1.5 TR (nominal capacity), High wall mounted, Inverter Split type Air-conditioner with BEE star rating 5, consisting of non-ductable type indoor units (fan coil) with cord less remote control and one number out door unit comprising of compressor, cooling fan, copper condensing coil suitable for operation on single phase, 230 +/- 10% volts, 50 HZ, AC supply including installing the indoor (fan coil) unit and outdoor unit on wall on suitable stand, providing and fixing insulated copper piping (suction and discharge) and electrical connections with flexible copper cable of suitable size as per manufacturer's recommendations, between the indoor and outdoor units up to a length of 3 (three) meters, wrapping the insulated refrigerant line with white wrapping tape, providing drain piping (up to 3 meter length), drilling the hole on wall, making good the opening after installation including first charge of refrigerant etc. complete as required. | 2.00 | Each |  | 45859.00 | 91718.00 | 55000.00 | 110000.00 | 81339.00 | 162678.00 | 45000.00 | 90000.00 | 65000.00 | 130000.00 | 42999.00 | 85998.00 | 85998.00 | DElite System Engineering (India) Pvt. Ltd.
5.02 | Supply and Installation of Copper pipe for the following capacity Air conditioners including suction and delivery copper pipes with all accessories such as insulation, power & control cabling, etc., complete as required
5.03 | For 1.5 TR Split Air conditioner (beyond 3 meters per Split AC unit) | 10.00 | Mtr |  | 1279.00 | 12790.00 | 2000.00 | 20000.00 | 1261.00 | 12610.00 | 1300.00 | 13000.00 | 1200.00 | 12000.00 | 1299.00 | 12990.00 | 12000.00 | DEEPAKELECTRICALS
5.04 | SITC of following capacity voltage stabilisers with copper wound coil having range of 170 to 270 voltage single phase, 50 Hz AC supply i/c necessary fixing arrangements, clamps, screws, metal clad top, connecting 3 core cable of 1 metre length, complete etc. as required.
5.05 | 4 KVA stabilizer for 1.5 TR Spilt AC | 2.00 | Each |  | 2669.00 | 5338.00 | 5000.00 | 10000.00 | 4244.00 | 8488.00 | 6000.00 | 12000.00 | 4500.00 | 9000.00 | 1999.00 | 3998.00 | 3998.00 | DElite System Engineering (India) Pvt. Ltd.
5.06 | Supplying & laying of condensate water drain pipe of ISI make PVC pipe having size of 40mm dia, 6kg/Cm² capacity along with 9 mm thick insulation for additional requirement for AC units i/c necessary clamps, screws, supports etc., complete etc. as required | 15.00 | Mtr |  | 499.00 | 7485.00 | 100.00 | 1500.00 | 388.00 | 5820.00 | 100.00 | 1500.00 | 100.00 | 1500.00 | 120.00 | 1800.00 | 1500.00 | Balaji Engineering, Limra Electricals, DEEPAKELECTRICALS
5.07 | Provision of Floor mounted water purifier cum dispenser having purification of 10 LPH with RO+UV or RO+ESS purification, stainless steel 304 grade storage tank for Normal/Cold/Hot with each of 8 Ltrs/3.3 Ltrs/1.1 Ltr storage capacity respectively, dynamic LCD display for monitoring of TDS, Catridge life, Temperature etc., 3 Nos. of stainless steel taps for Normal/Cold/Hot water, suitable for input water TDS of upto 1000 PPM, including with necessary piping arrangements for water intake and drain, operating at 230 V, 1-Phase, AC supply. etc ., complete as required. | 1.00 | Each |  | 53259.00 | 53259.00 | 100000.00 | 100000.00 | 82450.00 | 82450.00 | 60000.00 | 60000.00 | 55000.00 | 55000.00 | 79000.00 | 79000.00 | 53259.00 | CHENNAI ENGINEERING SERVICES
5.08 | Supply of Hot, Cold and Normal top Loaded Water Dispenser with nominal cooling capacity 2 Ltr./ Hr (min) and nominal Heating capacity 4 Ltr/ Hr (min). suitable for operation on 230 V+/- 10% single phase, 50 Hz AC supply etc., as required. | 2.00 | Each |  | 9759.00 | 19518.00 | 20000.00 | 40000.00 | 10670.00 | 21340.00 | 60000.00 | 120000.00 | 19000.00 | 38000.00 | 9999.00 | 19998.00 | 19518.00 | CHENNAI ENGINEERING SERVICES
6.00 | SH-VI : Internal Electrical works, Earthing and other Misc Items
6.01 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS/HFFR PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit, with piano type switch, phenolic laminated sheet, suitable size M.S. box and earthing the point with 1.5 sq.mm. FRLS/HFFR PVC insulated copper conductor single core cable etc. as required.
6.02 | Group C | 25.00 | Point |  | 1889.00 | 47225.00 | 1800.00 | 45000.00 | 1407.00 | 35175.00 | 1000.00 | 25000.00 | 1100.00 | 27500.00 | 899.00 | 22475.00 | 22475.00 | DElite System Engineering (India) Pvt. Ltd.
6.03 | Rewiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS/HFFR PVC insulated copper conductor single core cable and 1.5 sq.mm FRLS/HFFR PVC insulated copper conductor single core cable as earth wire in existing surface/recessed steel/PVC conduit including dismantling as required.
6.04 | Group C | 25.00 | Point |  | 1069.00 | 26725.00 | 1800.00 | 45000.00 | 1504.00 | 37600.00 | 800.00 | 20000.00 | 800.00 | 20000.00 | 399.00 | 9975.00 | 9975.00 | DElite System Engineering (India) Pvt. Ltd.
6.05 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS/HFFR PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required.
6.06 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 150.00 | Mtr |  | 369.00 | 55350.00 | 300.00 | 45000.00 | 218.00 | 32700.00 | 201.00 | 30150.00 | 250.00 | 37500.00 | 349.00 | 52350.00 | 30150.00 | Limra Electricals
6.07 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 100.00 | Mtr |  | 389.00 | 38900.00 | 400.00 | 40000.00 | 276.00 | 27600.00 | 250.00 | 25000.00 | 350.00 | 35000.00 | 409.00 | 40900.00 | 25000.00 | Limra Electricals
6.08 | Supplying and drawing following sizes of FRLS/HFFR PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
6.09 | 3 x 1.5 sq. mm | 100.00 | Mtr |  | 119.00 | 11900.00 | 250.00 | 25000.00 | 102.00 | 10200.00 | 120.00 | 12000.00 | 167.00 | 16700.00 | 99.00 | 9900.00 | 9900.00 | DElite System Engineering (India) Pvt. Ltd.
6.10 | 3 x 2.5 sq. mm | 150.00 | Mtr |  | 169.00 | 25350.00 | 300.00 | 45000.00 | 165.00 | 24750.00 | 170.00 | 25500.00 | 237.00 | 35550.00 | 129.00 | 19350.00 | 19350.00 | DElite System Engineering (India) Pvt. Ltd.
6.11 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
6.12 | 20 mm | 30.00 | Mtr |  | 139.00 | 4170.00 | 125.00 | 3750.00 | 49.00 | 1470.00 | 150.00 | 4500.00 | 65.00 | 1950.00 | 149.00 | 4470.00 | 1470.00 | vk sam engineering
6.13 | 25 mm | 30.00 | Mtr |  | 149.00 | 4470.00 | 150.00 | 4500.00 | 68.00 | 2040.00 | 150.00 | 4500.00 | 85.00 | 2550.00 | 169.00 | 5070.00 | 2040.00 | vk sam engineering
6.14 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc. as required.
6.15 | 75 mm X 75 mm X 60 mm deep (2 module equivalent) | 5.00 | Each |  | 189.00 | 945.00 | 350.00 | 1750.00 | 170.00 | 850.00 | 250.00 | 1250.00 | 65.00 | 325.00 | 450.00 | 2250.00 | 325.00 | DEEPAKELECTRICALS
6.16 | 100 mm X 100 mm X 60 mm deep (3 module equivalent) | 5.00 | Each |  | 209.00 | 1045.00 | 400.00 | 2000.00 | 189.00 | 945.00 | 300.00 | 1500.00 | 77.00 | 385.00 | 450.00 | 2250.00 | 385.00 | DEEPAKELECTRICALS
6.17 | 150 mm X 75 mm X 60 mm deep (4 module equivalent) | 5.00 | Each |  | 219.00 | 1095.00 | 400.00 | 2000.00 | 257.00 | 1285.00 | 350.00 | 1750.00 | 99.00 | 495.00 | 450.00 | 2250.00 | 495.00 | DEEPAKELECTRICALS
6.18 | 180 mm X 100 mm X 60 mm deep (6 module equivalent) | 2.00 | Each |  | 249.00 | 498.00 | 500.00 | 1000.00 | 340.00 | 680.00 | 400.00 | 800.00 | 170.00 | 340.00 | 450.00 | 900.00 | 340.00 | DEEPAKELECTRICALS
6.19 | 200 mm X 125 mm X 60 mm deep (8 module equivalent) | 2.00 | Each |  | 319.00 | 638.00 | 600.00 | 1200.00 | 437.00 | 874.00 | 450.00 | 900.00 | 230.00 | 460.00 | 700.00 | 1400.00 | 460.00 | DEEPAKELECTRICALS
6.20 | 200 mm X 250 mm X 100 mm deep (16 module equivalent) | 1.00 | Each |  | 479.00 | 479.00 | 800.00 | 800.00 | 437.00 | 437.00 | 500.00 | 500.00 | 267.00 | 267.00 | 700.00 | 700.00 | 267.00 | DEEPAKELECTRICALS
6.21 | Supplying and fixing following piano type switch/ socket on the existing switch box/ cover including connections etc. as required.
6.22 | 5/6 amps switch | 50.00 | Each |  | 59.00 | 2950.00 | 300.00 | 15000.00 | 64.00 | 3200.00 | 100.00 | 5000.00 | 35.00 | 1750.00 | 99.00 | 4950.00 | 1750.00 | DEEPAKELECTRICALS
6.23 | 15/16 A switch | 5.00 | Each |  | 129.00 | 645.00 | 300.00 | 1500.00 | 136.00 | 680.00 | 150.00 | 750.00 | 76.00 | 380.00 | 199.00 | 995.00 | 380.00 | DEEPAKELECTRICALS
6.24 | 3 pin 5/6 A socket outlet | 15.00 | Each |  | 69.00 | 1035.00 | 350.00 | 5250.00 | 218.00 | 3270.00 | 100.00 | 1500.00 | 87.00 | 1305.00 | 109.00 | 1635.00 | 1035.00 | CHENNAI ENGINEERING SERVICES
6.25 | 6 pin 15/16 A socket outlet | 5.00 | Each |  | 139.00 | 695.00 | 350.00 | 1750.00 | 170.00 | 850.00 | 150.00 | 750.00 | 99.00 | 495.00 | 129.00 | 645.00 | 495.00 | DEEPAKELECTRICALS
6.26 | Supplying and fixing metal box of 150mm X 75mm X 60mm deep (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including providing and fixing 3 pin 5/6 A socket outlet and 5/6 A piano type switch, connections, painting etc. as required. | 5.00 | Each |  | 899.00 | 4495.00 | 500.00 | 2500.00 | 340.00 | 1700.00 | 200.00 | 1000.00 | 500.00 | 2500.00 | 799.00 | 3995.00 | 1000.00 | Limra Electricals
6.27 | Supplying and fixing metal box of 180mm X 100mm X 60mm deep (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including providing and fixing 6 pin 5/6 & 15/16 A socket outlet and 15/16 A piano type switch, connections, painting etc. as required. | 5.00 | Each |  | 999.00 | 4995.00 | 500.00 | 2500.00 | 873.00 | 4365.00 | 200.00 | 1000.00 | 690.00 | 3450.00 | 900.00 | 4500.00 | 1000.00 | Limra Electricals
6.28 | Supply, Installation, testing and commissioning of 3-phase, 440V, 2 HP DOL starter suitable for rolling shutter including dismantling of existing stareter. | 6.00 | Each |  | 2999.00 | 17994.00 | 5000.00 | 30000.00 | 5820.00 | 34920.00 | 5000.00 | 30000.00 | 2500.00 | 15000.00 | 4000.00 | 24000.00 | 15000.00 | DEEPAKELECTRICALS
6.29 | Supply and laying of 3C X 2.5 Sqmm flexible copper cable with suitable clamping for street lights in terrace etc., as required. | 200.00 | Mtr |  | 229.00 | 45800.00 | 300.00 | 60000.00 | 222.00 | 44400.00 | 200.00 | 40000.00 | 200.00 | 40000.00 | 299.00 | 59800.00 | 40000.00 | Limra Electricals, DEEPAKELECTRICALS
6.30 | Supplying and fixing following way, IP43, Horizontal type three pole and neutral, sheet steel, MCB distribution board, on surface/recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted suitable for operation on 415V, 50Hz, three phase AC supply inline with technical specifications given in special conditions of contract including earthing etc. complete as required. (But without MCB/RCCB/Isolator) 8 way (4 + 24), Double door - Horizontal Type | 2.00 | Each |  | 8699.00 | 17398.00 | 10000.00 | 20000.00 | 8730.00 | 17460.00 | 6700.00 | 13400.00 | 14000.00 | 28000.00 | 9000.00 | 18000.00 | 13400.00 | Limra Electricals
6.31 | Supplying and fixing of following rating, four pole, 415 V, MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63 A, Four pole | 2.00 | Each |  | 2499.00 | 4998.00 | 2000.00 | 4000.00 | 1867.00 | 3734.00 | 2100.00 | 4200.00 | 2000.00 | 4000.00 | 2000.00 | 4000.00 | 3734.00 | vk sam engineering
6.32 | Supplying and fixing 40 amps rating, 240/415 volts, 'C' curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single Pole Neutral | 5.00 | Each |  | 1199.00 | 5995.00 | 300.00 | 1500.00 | 679.00 | 3395.00 | 1100.00 | 5500.00 | 650.00 | 3250.00 | 900.00 | 4500.00 | 1500.00 | Balaji Engineering
6.33 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, 'C' curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | 20.00 | Each |  | 329.00 | 6580.00 | 250.00 | 5000.00 | 218.00 | 4360.00 | 200.00 | 4000.00 | 190.00 | 3800.00 | 499.00 | 9980.00 | 3800.00 | DEEPAKELECTRICALS
6.34 | Dismantling of existing LT Panel as detailed below including dismantling of Power cabling, earthing etc. and Handing Over of dismantled materials to AAI Store etc. complete as required and as per the instructions of the Engineer-In-Charge. (Location : MT Section - Ground Floor & First Floor) i) LT Panel - 1 No ii) 8Way DB - 2 Nos iii) Hight bay light - 35Nos iv) Air Circulator Wall Fan - 07Nos | 1.00 | Job |  | 9999.00 | 9999.00 | 5000.00 | 5000.00 | 6790.00 | 6790.00 | 10000.00 | 10000.00 | 15000.00 | 15000.00 | 5000.00 | 5000.00 | 5000.00 | DElite System Engineering (India) Pvt. Ltd., Balaji Engineering
7.00 | Earthing
7.01 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 Meter long etc. with charcoal/ coke and salt as required. | 2.00 | Set |  | 7499.00 | 14998.00 | 12500.00 | 25000.00 | 8245.00 | 16490.00 | 10000.00 | 20000.00 | 13000.00 | 26000.00 | 9999.00 | 19998.00 | 14998.00 | CHENNAI ENGINEERING SERVICES
7.02 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | Mtr |  | 499.00 | 14970.00 | 450.00 | 13500.00 | 679.00 | 20370.00 | 250.00 | 7500.00 | 165.00 | 4950.00 | 399.00 | 11970.00 | 4950.00 | DEEPAKELECTRICALS
7.03 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 30.00 | Mtr |  | 249.00 | 7470.00 | 150.00 | 4500.00 | 223.00 | 6690.00 | 250.00 | 7500.00 | 170.00 | 5100.00 | 199.00 | 5970.00 | 4500.00 | Balaji Engineering
| Total in Figures |  |  |  |  | 2887877.00 |  | 2782150.00 |  | 3092856.00 |  | 3071390.00 |  | 3192222.00 |  | 3069650.00
Lowest Amount Quoted BY: Balaji Engineering(2782150.00)

## BOQ Summary
BOQ Summary Details Tender Title: Renovation of Electrical Works and its Allied Works at MT Section RHQ SR Chennai Airport Tender ID: 2026_AAI_286551_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Balaji Engineering (BID ID -1063827) | 2782150.00 | L1
| 2 | CHENNAI ENGINEERING SERVICES (BID ID -1062044) | 2887877.00 | L2
| 3 | DElite System Engineering (India) Pvt. Ltd. (BID ID -1062424) | 3069650.00 | L3
| 4 | Limra Electricals (BID ID -1064003) | 3071390.00 | L4
| 5 | vk sam engineering (BID ID -1063918) | 3092856.00 | L5
| 6 | DEEPAKELECTRICALS (BID ID -1064029) | 3192222.00 | L6