## BoQ1
Government eProcurement System Created By: Ramroop Meena Created Date/Time: 08-Sep-2026 01:10 PM Tender Title: SITC of AC units at 1st floor area of NTB, VIP,CIP, server room and PBBs at NTB at Khajuraho Airport. Tender ID: 2026_AAI_286735_1
Tender Inviting Authority: Asst. General Manager (Engg.-Electrical), Airports Authority of India, Khajuraho Airport.
Name of Work: SITC of AC units at 1st floor area of NTB, VIP,CIP, server room and PBB's at NTB at Khajuraho Airport.
Tender Id: 2026_AAI_286735_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | VOLGA AIR TECHNOLOGIES INDIA (GSTN-23AFGPC9885C1ZC) BID ID -1060841 |  | Anoop Refrigeration (GSTN-09AAGFA4646N1Z1) BID ID -1061479 |  | VOLKS ENERGIE PVT LTD (GSTN-07AADCV9396C1ZZ) BID ID -1061501 |  | A 2ENTERPRISES (GSTN-NA) BID ID -1061263 |  | AIR DESIGN SOLUTIONS (GSTN-NA) BID ID -1062267
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | VRV/VRF OUT DOOR UNITS Supply, Installation, testing & commissioning of variable refrigerent volume / flow modulur type Heat Pump (Heating & Cooling type) outdoor unit equiped with highly efficient hermetically sealed rotary /scroll type inverter compressor(s) with 16 HP onwards having multiple compressor, special heat exchanger, y branch unit support, auto check function for connection error, Refrigerant R-410A, with Variable refrigerant temperature, auto gas charging facility for proper gas charging / as per OEM, refrigerant cooled PCB for long life of PCB/as per OEM. The EER at 100% load shall not be less than 3.73 for 16 HP outdoor unit heat pump suitable to operate from 380-415 volt, 50 Hz,3 phase AC power supply complete with individual controller and fittings with factory wired, tested with all neccessary controls and filled with first charge of refrigerent before delivering at site , connection & termination including complete as per enclosed technical specifications. Outdoors units of the VRV system shall be compact air cooled type.The outdoor units shall be suitable to operate within an ambient temperature range of "-5 Deg C to 53 Deg C" in cooling mode; & "-15 Deg C to 15.5 Deg C" in heating mode. All Outdoor units above 16 HP should have atleast 2 condensor Fans with top discharge arrangement. The VRV/VRF units must be capable so that refrigerent piping between outdoor unit & the indoor units shall be extendable up to 165 Meter with maximum level difference between outdoor unit & indoor units of 90 m and level difference between two indoor units shall be maximum up to 30 Meter . The compressor should be OEM manufactured/ as per OEM of unit. Including supply and installation of painted suitable size and strength MS frame/stand for outdoor unit etc complete as required.
1.01 | 76 HP | 2.00 | Set | 1.00 | 1389336.00 | 2778672.00 | 1568920.00 | 3137840.00 | 1520000.00 | 3040000.00 | 1388915.00 | 2777830.00 | 1364960.00 | 2729920.00 | 2729920.00 | AIR DESIGN SOLUTIONS
2.00 | VRV/VRF OUT DOOR UNITS Supply, Installation, testing & commissioning of of variable refrigerent volume / flow modulur type Heat Pump (Heating & Cooling type) outdoor unit equiped with highly efficient hermetically sealed rotary/scroll type inverter compressor(s) , special heat exchanger, y branch unit support, auto check function for connection error, Refrigerant R-410A, with Variable refrigerant temperature, auto gas charging facility for proper gas charging/ as per OEM, refrigerant cooled PCB for long life of PCB/as per OEM.The EER at 100% load shall not be less than 3.60 for 6 HP out door unit heat pump suitable to operate from 380-415 volt, 50 Hz,3 phase AC power supply complete with individual controller and fittings with factory wired, tested with all neccessary controls and filled with first charge of refrigerent before delivering at site , connection & termination, including complete as per enclosed technical specifications. Outdoors units of the VRV system shall be compact air cooled type.The outdoor units shall be suitable to operate within an ambient temperature range of "-5 Deg C to 53 Deg C" in cooling mode; & "-15 Deg C to 15.5 Deg C" in heating mode. The VRV/VRF units must be capable so that refrigerent piping between outdoor unit & the indoor units shall be extendable up to 50 Meter with maximum level difference between outdoor unit & indoor units of 30 meter. The compressor should be OEM manufactured/as per OEM of unit. Including supply and installation of painted suitable size and strength MS frame/stand for outdoor unit etc complete as required.
2.01 | 6 HP | 2.00 | Set | 1.00 | 174460.00 | 348920.00 | 281250.00 | 562500.00 | 180000.00 | 360000.00 | 171325.00 | 342650.00 | 149270.00 | 298540.00 | 298540.00 | AIR DESIGN SOLUTIONS
3.00 | SITC of Factory built and Site assembled floor mounted Vertical AHU with Top Discharge as mentioned below, Dx type double skin air handing units complete as per specifications and of following capacities. Double skin construction : Inner skin 0.8 mm GI and outer skin 0.6 mm thick precoated GI. Thickness of insulation- 45 mm CFC free PUF injected with density of 40+/-42 kg/cum. Frame work: Thermal break aluminium profile with thermal barrier & Coving. Unit Base: Heavy Duty GSS FA Al Damper: Manual Gear operated FA Damper with 10 micron filter. (Fresh air opening should have 10 micron pre-filter.) RA Al Damper: Manual Gear Operated RA damper. Fan Section: 1- Running DIDW Backward curved centrigugal Fan with suitable capacity IE-3 motor (The Fan Section to be provided with double glass view window, light fixtures and Limit switch), Screen protection door, fire proof double canvass connections (Fungal Resistant and Lint free). Drain pan : stainless steel duly insulated with 13 mm thick nitrile rubber / cross linked polyethylene Vertical AHU with TOP Discharge, 8 row deep Dx cooling coil. (Coil dia min. 12/15 mm) (Coil Surface area ≤ 500 FPM) Header Material : Copper No. of Fins per inch (FPI) 11 / 12 Coil Casing / Blank offs : SS-304, Independedt Pre Filter Section , SA section with manual gear operated SA damper., All dampers shall be Aerofoil & gear type with lock & graduation arrangement. Complete Units shall be mounted on suitably rated neoprene pads. AHU Kit: AHU Kits along with suitable starters
3.01 | Capacity - 15 TR/6000 CFM/60 mm Static | 8.00 | Set | 1.00 | 375091.00 | 3000728.00 | 510000.00 | 4080000.00 | 300000.00 | 2400000.00 | 408000.00 | 3264000.00 | 243225.00 | 1945800.00 | 1945800.00 | AIR DESIGN SOLUTIONS
4.00 | VRV/VRF Ceiling mounted Indoor Unit Supply, Installation, testing & commissioning of VRV/VRF ceiling mounted type indoor Unit ( Cooling and heating type) of following capacity including fan section with airflow range from low to high 812 to 1600 CFM ,pre filters, DX coil section, safety devices , sensors for different features ,standard accessories etc. complete as required suitable to operate from 220 V to 240 V , 50 HZ, single phase power supply with corded remote control, fittings etc. , maximum noise level should not be more than 55 DBA . The unit shall have external asthetic panel for supply and return air etc. complete as required. It includes all the MS angle/ channel/GI threaded rod etc. of suitable size and strength , fastner , nut bolts, washers etc. drilling , cutting including all civil works and making same good complete to install the unit from the ceiling.
4.01 | 4.0 TR Four Way Cassette unit | 2.00 | Set | 1.00 | 42600.00 | 85200.00 | 68200.00 | 136400.00 | 55000.00 | 110000.00 | 49940.00 | 99880.00 | 41250.00 | 82500.00 | 82500.00 | AIR DESIGN SOLUTIONS
5.00 | Supply, installation, testing and commissioning of following capacity Air-cooled Tower/ Standing Type Air Conditioner Unit (both indoor & outdoor complete) alongwith vibration isolator, as per latest BEE Standard fitted with 100% copper condensing unit comprising of sealed rotary type compressor with Inverter Technology and Non CFC refrigerant like R32/ R410A suitable for stabilizer free operation at 3ph, 415V, 50Hz AC supply etc. as required.
5.01 | 4.0 TR Tower AC unit | 2.00 | Set | 1.00 | 144539.00 | 289078.00 | 143775.00 | 287550.00 | 150000.00 | 300000.00 | 119250.00 | 238500.00 | 119900.00 | 239800.00 | 238500.00 | A 2ENTERPRISES
6.00 | Ductable Split AC Units Supply, Installation, testing & commissioning of following capacity micro processor based aircoled ductable type, 3 phase split airconditioners with evaporator coil, fan and fan motor, aircoled condenser, with hermatically sealed scroll compressor, DX condenser coil, pre-filter & expansion valve, flexible canvass connections suitable electrical wiring, steel frame, MS stand for ODU i/c filling of suitable refrigerant gas, pressure testing, etc. complete as required.
6.01 | 16.5 TR | 3.00 | Set | 1.00 | 332425.00 | 997275.00 | 395550.00 | 1186650.00 | 400000.00 | 1200000.00 | 299000.00 | 897000.00 | 317350.00 | 952050.00 | 897000.00 | A 2ENTERPRISES
7.00 | Supply, Installation, testing and commissioning of necessary fittings, Refnet-joints and headers etc. along with all the accessories complete as required . | 12.00 | Set | 1.00 | 4860.00 | 58320.00 | 5600.00 | 67200.00 | 3000.00 | 36000.00 | 3850.00 | 46200.00 | 4070.00 | 48840.00 | 36000.00 | VOLKS ENERGIE PVT LTD
8.00 | Supply and charging /filling of Refrigerant R-410A as per length of copper pipe as per site requirement . | 150.00 | Kg | 1.00 | 1188.00 | 178200.00 | 1875.00 | 281250.00 | 150.00 | 22500.00 | 1150.00 | 172500.00 | 1155.00 | 173250.00 | 22500.00 | VOLKS ENERGIE PVT LTD
9.00 | Refrigerant Piping Supply , Installation, testing and commisioning of interconnecting following sizes of one end expanded refrigerant copper pipe work of following outer diameter ( Nominal size/as recommended by OEM, if higher size than mentioned size ( 28.6/15.9 for 20 HP and 22.2/9.5 for 10 HP) is recommended by OEM , same is acceptable ,however, payment shall be made as per mentioned size), insulated with 19/13 mm thick closed cell electrometric EPDM/nitrile rubber tubular insulation between each set of indoor & outdoor units with outer mechanical protection of alluminum cladding of minimum 1.5 mm. thick of suitable size for all exposed pipes inside and outside the room as per specification. All piping inside and outside of the room shall be propelrly fixed/supported with suitable size of clamp/ M.S. hanger complete as required at site.( Whereever pipes to be laid in cable tray same shall be paid as extra )
9.01 | 28.6 mm dia and 1.00 mm thick with 19 mm thick EPDM/nitrile rubber insulation | 200.00 | Mtrs. | 1.00 | 2486.00 | 497200.00 | 2072.00 | 414400.00 | 1500.00 | 300000.00 | 1550.00 | 310000.00 | 1363.00 | 272600.00 | 272600.00 | AIR DESIGN SOLUTIONS
9.02 | 22.2 mm dia and 0.8 mm thick with 19mm thick EPDM/nitrile rubber insulation | 50.00 | Mtrs. | 1.00 | 1619.00 | 80950.00 | 1898.00 | 94900.00 | 700.00 | 35000.00 | 1250.00 | 62500.00 | 900.00 | 45000.00 | 35000.00 | VOLKS ENERGIE PVT LTD
9.03 | 19.1 mm dia 0.8 mm thick with 13mm thick EPDM/nitrile rubber insulation | 50.00 | Mtrs. | 1.00 | 1266.00 | 63300.00 | 1668.00 | 83400.00 | 800.00 | 40000.00 | 1250.00 | 62500.00 | 755.00 | 37750.00 | 37750.00 | AIR DESIGN SOLUTIONS
9.04 | 15.9 mm dia and 0.8 mm thick with 13mm thick EPDM/nitrile rubber insulation | 250.00 | Mtrs. | 1.00 | 954.00 | 238500.00 | 1093.00 | 273250.00 | 620.00 | 155000.00 | 800.00 | 200000.00 | 765.00 | 191250.00 | 155000.00 | VOLKS ENERGIE PVT LTD
9.05 | 12.7 mm dia and 0.8 mm thick with 13mm thick EPDM/ nitrile rubber insulation | 50.00 | Mtrs. | 1.00 | 779.00 | 38950.00 | 863.00 | 43150.00 | 300.00 | 15000.00 | 592.00 | 29600.00 | 508.00 | 25400.00 | 15000.00 | VOLKS ENERGIE PVT LTD
9.06 | 9.5 mm dia 0.8 mm thick with 13mm thick EPDM/nitrile rubber insulation | 100.00 | Mtrs. | 1.00 | 588.00 | 58800.00 | 748.00 | 74800.00 | 20.00 | 2000.00 | 400.00 | 40000.00 | 383.00 | 38300.00 | 2000.00 | VOLKS ENERGIE PVT LTD
10.00 | Drain Piping Providing & fixing of PVC Pipe complete with fittings, supports as per specifications and duly insulated with closed cell nitrile rubber as per direction of Engineer-in-charge & specifications enclosed as reqd.
10.01 | 40 mm dia with 6 mm thick insulation | 80.00 | Mtrs. | 1.00 | 91.00 | 7280.00 | 546.00 | 43680.00 | 150.00 | 12000.00 | 350.00 | 28000.00 | 150.00 | 12000.00 | 7280.00 | VOLGA AIR TECHNOLOGIES INDIA
10.02 | 32 mm dia with 6 mm thick insulation | 80.00 | Mtrs. | 1.00 | 156.00 | 12480.00 | 443.00 | 35440.00 | 130.00 | 10400.00 | 250.00 | 20000.00 | 125.00 | 10000.00 | 10000.00 | AIR DESIGN SOLUTIONS
10.03 | 25 mm dia with 6 mm thick insulation | 50.00 | Mtrs. | 1.00 | 130.00 | 6500.00 | 316.00 | 15800.00 | 30.00 | 1500.00 | 185.00 | 9250.00 | 100.00 | 5000.00 | 1500.00 | VOLKS ENERGIE PVT LTD
11.00 | Control & Transmission Wiring Supply & laying of suitable size PVC conduit and control cum transmission wiring of 2 core x 1.0 sqmm copper between indoor and out door unit. | 450.00 | Mtrs. | 1.00 | 143.00 | 64350.00 | 106.00 | 47700.00 | 100.00 | 45000.00 | 125.00 | 56250.00 | 100.00 | 45000.00 | 45000.00 | VOLKS ENERGIE PVT LTD, AIR DESIGN SOLUTIONS
12.00 | Supply & fixing / Laying of M S Slotted Angle for pipes and cables horizontaly and vertically along with MS / GI channel, angle ,threaded rod, anchor fastner ,nut, bolt, saddle, tie etc.complete as required. | 200.00 | Mtrs. | 1.00 | 228.00 | 45600.00 | 175.00 | 35000.00 | 16.00 | 3200.00 | 300.00 | 60000.00 | 200.00 | 40000.00 | 3200.00 | VOLKS ENERGIE PVT LTD
13.00 | Supply , fabrication and Installation of powder coated Un-Insulated Square/ Rectangular “GSS” supply air ducting complete along with all accessories as per the approved shop drawings.The color of powder coating shall be same of color of inddor unit of VRV/VRF system.
13.01 | 20 Gauge | 200.00 | Sq. Mtr. | 1.00 | 1620.00 | 324000.00 | 1900.00 | 380000.00 | 200.00 | 40000.00 | 1650.00 | 330000.00 | 950.00 | 190000.00 | 40000.00 | VOLKS ENERGIE PVT LTD
13.02 | 18 Gauge | 50.00 | Sq. Mtr. | 1.00 | 530.00 | 26500.00 | 2378.00 | 118900.00 | 4000.00 | 200000.00 | 1950.00 | 97500.00 | 1800.00 | 90000.00 | 26500.00 | VOLGA AIR TECHNOLOGIES INDIA
14.00 | Supply & fixing / Installation of acoustic lining of duct with XLPE sheet for the ducts with 25 mm thick one layer internally on duct complete as required | 250.00 | Sq. Mtr. | 1.00 | 346.00 | 86500.00 | 1093.00 | 273250.00 | 50.00 | 12500.00 | 850.00 | 212500.00 | 1200.00 | 300000.00 | 12500.00 | VOLKS ENERGIE PVT LTD
15.00 | Supply & fixing/ Installation of extruded aluminum powder coated supply air/Return air eye ball jet diffuser 315 mm in the existing duct etc. complete as required. | 35.00 | Each | 1.00 | 2625.00 | 91875.00 | 2888.00 | 101080.00 | 4000.00 | 140000.00 | 3250.00 | 113750.00 | 2420.00 | 84700.00 | 84700.00 | AIR DESIGN SOLUTIONS
16.00 | Supply & Installation charges for Canvass connection between indoor unit and supply air duct complete as required . | 8.00 | Each | 1.00 | 2875.00 | 23000.00 | 2363.00 | 18904.00 | 250.00 | 2000.00 | 2500.00 | 20000.00 | 2000.00 | 16000.00 | 2000.00 | VOLKS ENERGIE PVT LTD
17.00 | Supply of XLPE insulated PVC sheathed Aluminium conductor armoured power cable of grade 1.1 KV generally confirming to IS:7098 part-I with utpo date amendments etc. as required of following size. 3.5 Core X 120 Sqmm | 200.00 | Mtrs. | 1.00 | 875.00 | 175000.00 | 525.00 | 105000.00 | 610.00 | 122000.00 | 650.00 | 130000.00 | 800.00 | 160000.00 | 105000.00 | Anoop Refrigeration
18.00 | Supply of 1100V PVC insulated & Sheathed with Bare Annealed Copper Conductor multi core flexible cable as per IS:694-2010 with utpo date amendments etc. as required of following size. 4 Core X 25 Sqmm. | 100.00 | Mtrs. | 1.00 | 2125.00 | 212500.00 | 437.00 | 43700.00 | 1550.00 | 155000.00 | 1150.00 | 115000.00 | 1837.00 | 183700.00 | 43700.00 | Anoop Refrigeration
19.00 | Supply of 1100V PVC insulated & Sheathed with Bare Annealed Copper Conductor multi core flexible cable as per IS:694-2010 with utpo date amendments etc. as required of following size. 4 Core X 10 Sqmm. | 650.00 | Mtrs. | 1.00 | 801.00 | 520650.00 | 330.00 | 214500.00 | 605.00 | 393250.00 | 780.00 | 507000.00 | 787.00 | 511550.00 | 214500.00 | Anoop Refrigeration
20.00 | Supply of 1100V PVC insulated & Sheathed with Bare Annealed Copper Conductor multi core flexible cable as per IS:694-2010 with utpo date amendments etc. as required of following size. 3 Core X 6 Sqmm. | 250.00 | Mtrs. | 1.00 | 353.00 | 88250.00 | 161.00 | 40250.00 | 270.00 | 67500.00 | 550.00 | 137500.00 | 363.00 | 90750.00 | 40250.00 | Anoop Refrigeration
21.00 | Electrical Panel: Outdoor Type LT Panel Design, fabrication, assembly, wiring and supply, erection, testing and commissioning of front operated cubicle type compartmentalised TTA Panel as per Form 4B, rear access free standing,dust and vermin proof (IP 55 ingress protection) main switchboards conforming to IEC-61439 suitable for use at 433 volts, 3 phase 4 wire 50 Hertz system suitable for a symmetrical fault level of 36kA (specified with the panel) at 433 volts, fabricated from 2 mm thick CRCA MS sheets with hinged, gasketted (metal based neoprene) and lockable doors having structural reinforcement with suitable angle/channel/T/flat sections including 3 mm thick gland plates on top / bottom and including lifting hooks and including earth strip of required size with 2 nos. earthing terminals and including Al Busbars of 600 Amps,36 KA/suitable higher rating and size i/c powder coated paint finish of approved shade over metal surface cleaned and treated with nine tank process complete with interconnections etc. as per specifications, as required below. The incoming and outgoing feeders shall be accommodated in a modular arrangement, detachable gland plates, adequate size cable alley, Sign writing, Painting, Earthing, Numbering, Danger plate, including PVC insulated copper FRLS wires of minimum 1.5sq.mm & 2.5sq.rnm for CT's etc., exhaust fan, door limit switch, space heater , MCBs for space heaters, thermostat, LED bulb holder with lamp with MCBs with all required materials complete as required as per specifications attached. Note:- All the accessories required to complete the system shall be of suitable rating and in required quantity . Incomer : 400A, FP MCCB 400A ,4P, 36kA MCCB microprocessor based electronic trip unit having adjustable LSIG protection ,Rear Spreader KIT rear terminal, Rotary Handle Operating Mechanism with door interlock, Auxiliary Contact, shunt trip (230V AC), Digital Multi-Function Meter LED Type 3 digit display(Parameters: V, I, Hz, PF, KW, KVA, KVAR, Total Energy, THDV, THDI & Run Hours) with RS 485, Auxiliary Contactor, 3-phase current transformers of suitable ratio and class, LED Indicating Lamps , MCBs, CT Shorting Link internal control wiring, termination, ferruling, labeling and all accessories, complete as required.-2 set Note:- All the accessories required shall be of suitable rating and in required quantity to complete the system. | 1.00 | Job | 1.00 | 849800.00 | 849800.00 | 580000.00 | 580000.00 | 800000.00 | 800000.00 | 275800.00 | 275800.00 | 825000.00 | 825000.00 | 275800.00 | A 2ENTERPRISES
21.01 | Bus coupler 400A ,4P, 36kA MCCB microprocessor based electronic trip unit having adjustable LSIG protection ,Rear Spreader KIT rear terminal, Rotary Handle Operating Mechanism with door interlock, Auxiliary Contact, shunt trip (230V AC), and LED Indicating Lamps ( ON/OFF/TRIP) , MCBs, internal control wiring, termination, ferruling, labeling and all accessories, complete as required. (Ground fault protection shall be provided but may be set to OFF if not required). The MCCB shall be complete with mechanical and electrical interlocking arrangement with both incomer MCCBs to prevent unsafe paralleling.-1 set Note:- All the accessories required shall be of suitable rating and in required quantity to complete the system. Outgoings 63A, 4P, 36kA MCCB with adjustable thermal & magnetic release, rotary handle operating mechanism with door interlock, auxiliary contacts, rear terminal kit, indicating lamps (ON, OFF, TRIP), control MCBs (2A, SP, MCB), complete as required -8 set Note:- All the accessories required shall be of suitable rating and in required quantity to complete the system. 40A, four pole, (three phaseand neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 300 mA complete as required - 10 SET 32 A, four pole, (three phaseand neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 300 mA complete as required - 03 SET 20 A, four pole, (three phaseand neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 300 mA complete as required - 03 SET
22.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories,and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Each | 1.00 | 18200.00 | 36400.00 | 20000.00 | 40000.00 | 2500.00 | 5000.00 | 17500.00 | 35000.00 | 22500.00 | 45000.00 | 5000.00 | VOLKS ENERGIE PVT LTD
23.00 | Percentage above or below to carry out works amounting to Rs. 5,00,000.00 by executing any items (items shall be chosen as per site requirement) listed in CPWD schedule of rates (Electrical) DSR-2025 as per CPWD specifications as and when required as per instructions of EIC. (Note:- 1.The firm has to quote the percentage above/below of the DSR-2025 in the form of multiplying factor on the quantity mentioned against this item as clarified below. For example: To quote 10% above the DSR-2025 rates, the rate column should be filled as Rs.550000/-, whereas to quote 10% below the DSR-2025 rates, the rate column should be filled as Rs. 450000/- Note:-2 The DSR rate shall be applicable for items which are not covered in above BOQ items 1 to 22 ) | 1.00 | Job | 1.00 | 131950.00 | 131950.00 | 450000.00 | 450000.00 | 425000.00 | 425000.00 | 450000.00 | 450000.00 | 600000.00 | 600000.00 | 131950.00 | VOLGA AIR TECHNOLOGIES INDIA
| Total in Figures |  |  |  |  | 11416728.00 |  | 13266494.00 |  | 10449850.00 |  | 11140710.00 |  | 10289700.00
Lowest Amount Quoted BY: AIR DESIGN SOLUTIONS(10289700.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of AC units at 1st floor area of NTB, VIP,CIP, server room and PBBs at NTB at Khajuraho Airport. Tender ID: 2026_AAI_286735_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | AIR DESIGN SOLUTIONS (BID ID -1062267) | 10289700.00 | L1
| 2 | VOLKS ENERGIE PVT LTD (BID ID -1061501) | 10449850.00 | L2
| 3 | A 2ENTERPRISES (BID ID -1061263) | 11140710.00 | L3
| 4 | VOLGA AIR TECHNOLOGIES INDIA (BID ID -1060841) | 11416728.00 | L4
| 5 | Anoop Refrigeration (BID ID -1061479) | 13266494.00 | L5