## BoQ1
Government eProcurement System Created By: Narendra Narayan Dubey Created Date/Time: 11-Sep-2026 01:53 PM Tender Title: Provision of UPS for GLF facilities at Kanpur Airport (Inclusive of AICMC for 6 Years after DLP of 2 years) Tender ID: 2026_AAI_286949_1
Tender Inviting Authority: Assistant. General Manager (E-E)
Name of Work: Provision of UPS for GLF facilities at Kanpur Airport (Inclusive of AICMC for 6 Years after DLP of 2 years).
Contract No: 2026_AAI_286949_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ECS ENGINEERING PVT LTD (GSTN-09AABCE5944P1Z1) BID ID -1064251 |  | SUN POWER CONVERSION PVT LTD (GSTN-09AAICS9074K1ZL) BID ID -1065374 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -1065751
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing, and Commissioning of 2 Nos. x 20 KVA online double conversion UPS systems based on PWM IGBT technology, configured for parallel redundant operation. The systems shall be suitable for 3-phase input at 50±10% Hz AC supply and shall provide a 3-phase output of 415V ± (0.5-1)%, conforming to the technical specifications of the tender document. The work includes interconnection between the UPS units and the battery bank, as well as interconnection between the UPS units for parallel operation by providing steel conduit, copper cables / wires of required size & lengths including laying. Both UPS systems shall operate simultaneously and share the load; in the event of failure of UPS-I, UPS-II shall take the full load, and vice versa, as required. (Note: 01 Job = 2 Nos. x 20 KVA UPS. The battery bank shall be installed in the adjacent room.) | 1.00 | Job |  | 728000.00 | 728000.00 | 599000.00 | 599000.00 | 350000.00 | 350000.00 | 350000.00 | Awasthi Electric Works
2.00 | Supply, installation, testing, and commissioning of a Battery Bank to provide uninterrupted power backup for at least 30 minutes at full load (for each UPS mentioned in Sl. No. 1). The battery bank shall consist of a sufficient number of VRLA SMF batteries of suitable AH capacity, calculated as per OEM recommendations, including all necessary connections and interconnections as per site requirements. Each battery bank shall be provided with an isolation breaker. The battery bank is to be installed on a painted MS battery rack/stand of adequate strength and size, suitable for multi-layer storage and designed to fit within the available room size (approximately 14 feet x 6 feet). (Note: 01 Set Battery Bank = Total No. of Batteries required for each single UPS for 30 minutes backup on full load) | 2.00 | Set |  | 126118.00 | 252236.00 | 167500.00 | 335000.00 | 225000.00 | 450000.00 | 252236.00 | ECS ENGINEERING PVT LTD
3.00 | Design, supply, installation, testing, and commissioning of an indoor, floor-mounted LT panel suitable for operation at 415V, 50Hz, 3-phase, 4-wire system. Bus bar shall be made of Aluminium of suitable size and capacity.The panel shall be fabricated from 2 mm thick CRCA sheet, duly powder-coated, and shall have IP-42 degree of protection. It shall be mounted on a stand of suitable height to facilitate bottom cable entry and shall be provided with a 3 mm thick detachable gland plate. The panel shall consist of the following: Incomer : a) Incoming feeders (3-Phase, 100A TPN MCCB, 25kA) with suitable size aluminium busbars with insulation sleeves., voltmeter, ammeter with selector switches, indication lamps and control wiring- 02 Nos. Bus Coupler : b) Bus Coupler (TPN MCCB, 100A, 25kA) with mechanical interlocking arrangement and necessary control wiring- 01 Nos. Outgoing : c) 32A MCB controlled single Phase Output feeders with rotary switch- 04 Nos. d) Single Phase Output DP MCBs (32A)- 02 Nos e) 63A TPN MCCBs with suitable space for termination of 3.5 x 120 sq.mm Aluminum armoured cable - 03 Nos. f) Internal wiring, indication lamps on incoming and outgoing, ferruling, earthing terminals, and appropriate cable dressing and labelling for all incomer, bus coupler and outgoing feeders complete as required. | 1.00 | Job |  | 176471.00 | 176471.00 | 90000.00 | 90000.00 | 130000.00 | 130000.00 | 90000.00 | SUN POWER CONVERSION PVT LTD
4.00 | Supply and fixing of class A electrical insulation mats confirming to IS 15652 of thickness minimum 2.0mm with shock proof of size 1mtr X 2mtrs (or as per site requirement) complete as required. | 20.00 | Sq.mtr |  | 824.00 | 16480.00 | 675.00 | 13500.00 | 850.00 | 17000.00 | 13500.00 | SUN POWER CONVERSION PVT LTD
5.00 | Supply, installation, testing, and commissioning (SITC) of 1.5 TR BEE 5-star rated high wall split inverter air conditioner, complete with inverter compressor, suitable for operation on 230V ±10% AC power supply. The job includes the provision and installation of suction and discharge copper pipes of appropriate size with insulation, PVC insulated and sheathed multicore copper conductor power cable from indoor to outdoor unit and a drain pipe of required length. The outdoor unit shall be installed on a suitably sized MS stand as per site requirements. The scope of work also includes any minor civil works necessary for proper installation, making the job complete in all respects. | 2.00 | Job |  | 47059.00 | 94118.00 | 35000.00 | 70000.00 | 41500.00 | 83000.00 | 70000.00 | SUN POWER CONVERSION PVT LTD
6.00 | Supply, installation, testing, and commissioning of automatic changeover timer capable of switching operation between two split AC units (item no. 5) alternately at a programmable interval of 2 to 8 hours including wiring, connectins etc. as required. | 1.00 | Job |  | 2588.00 | 2588.00 | 2500.00 | 2500.00 | 8000.00 | 8000.00 | 2500.00 | SUN POWER CONVERSION PVT LTD
7.00 | Supply, Installation, Testing and Commissioning of single phase automatic voltage stabilizer, suitable for operation of 1.5 TR inverter-type high-wall split air conditioner. The stabilizer shall have an input voltage range of 170V to 270V and output voltage of 230V ±1%. It shall be wall-mountable, with digital display for input and output voltage, built-in time delay system, over-voltage and under-voltage cut-off and thermal overload protection. The job includes all accessories, hardware, interconnections and civil works (if any) for proper installation and commissioning, complete as required. | 2.00 | Job |  | 2588.00 | 5176.00 | 4000.00 | 8000.00 | 7000.00 | 14000.00 | 5176.00 | ECS ENGINEERING PVT LTD
8.00 | Supply of 4 C x 16 sqmm, 1.1 KV grade XLPE insulated, PVC sheathed, armoured copper conductor cable conforming to IS 7098 (Part 1) amended up to date. | 70.00 | Mtr |  | 1224.00 | 85680.00 | 1095.00 | 76650.00 | 1200.00 | 84000.00 | 76650.00 | SUN POWER CONVERSION PVT LTD
9.00 | Supply of 4 C x 16 sqmm, 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor cable conforming to IS 7098 (Part 1) amended up to date. | 35.00 | Mtr |  | 208.00 | 7280.00 | 179.00 | 6265.00 | 200.00 | 7000.00 | 6265.00 | SUN POWER CONVERSION PVT LTD
10.00 | Supply and fixing of 100 Amp, Four Pole, 415 Volts Isolator in a suitable enclosure box, complete with necessary connections, testing and commissioning as required, suitable for wall mounting as required. | 2.00 | Each |  | 1765.00 | 3530.00 | 1500.00 | 3000.00 | 1200.00 | 2400.00 | 2400.00 | Awasthi Electric Works
11.00 | Laying of one number PVC/XLPE insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry duct as required. (up to 35 sqmm) | 135.00 | Mtr |  | 47.00 | 6345.00 | 50.00 | 6750.00 | 40.00 | 5400.00 | 5400.00 | Awasthi Electric Works
12.00 | Supplying and making end termination with brass compression gland and copper lugs for following size of PVC/XLPE insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required. 4 X 16 sq. mm (28mm) | 4.00 | Set |  | 412.00 | 1648.00 | 2000.00 | 8000.00 | 500.00 | 2000.00 | 1648.00 | ECS ENGINEERING PVT LTD
13.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC/XLPE insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 120 sq. mm (45mm) | 2.00 | Set |  | 588.00 | 1176.00 | 4000.00 | 8000.00 | 800.00 | 1600.00 | 1176.00 | ECS ENGINEERING PVT LTD
14.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC/XLPE insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3 X 10 sq. mm (22mm) | 3.00 | Set |  | 235.00 | 705.00 | 2000.00 | 6000.00 | 300.00 | 900.00 | 705.00 | ECS ENGINEERING PVT LTD
15.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer ) as required. 4 way (4 + 12), Double door | 1.00 | Each |  | 3647.00 | 3647.00 | 9000.00 | 9000.00 | 10500.00 | 10500.00 | 3647.00 | ECS ENGINEERING PVT LTD
16.00 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63 Amps | 1.00 | Each |  | 1806.00 | 1806.00 | 1000.00 | 1000.00 | 1000.00 | 1000.00 | 1000.00 | SUN POWER CONVERSION PVT LTD, Awasthi Electric Works
17.00 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole ( 32A- 8 Nos, 20 Amp- 4 Nos) | 12.00 | Each |  | 169.00 | 2028.00 | 125.00 | 1500.00 | 250.00 | 3000.00 | 1500.00 | SUN POWER CONVERSION PVT LTD
18.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.(Group C) | 6.00 | Point |  | 2588.00 | 15528.00 | 500.00 | 3000.00 | 1800.00 | 10800.00 | 3000.00 | SUN POWER CONVERSION PVT LTD
19.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required. (Group C) | 5.00 | Point |  | 2588.00 | 12940.00 | 700.00 | 3500.00 | 1000.00 | 5000.00 | 3500.00 | SUN POWER CONVERSION PVT LTD
20.00 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required
20.01 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 30.00 | Meter |  | 529.00 | 15870.00 | 50.00 | 1500.00 | 275.00 | 8250.00 | 1500.00 | SUN POWER CONVERSION PVT LTD
20.02 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 70.00 | Meter |  | 600.00 | 42000.00 | 50.00 | 3500.00 | 350.00 | 24500.00 | 3500.00 | SUN POWER CONVERSION PVT LTD
20.03 | 2 X 6 sq. mm + 1 X 6 sq. mm earth wire | 50.00 | Meter |  | 927.00 | 46350.00 | 50.00 | 2500.00 | 475.00 | 23750.00 | 2500.00 | SUN POWER CONVERSION PVT LTD
21.00 | Supplying and fixing following size/ modules, GI box along with modular base & cover plate for modular switches in recess etc as required.
21.01 | 3 Module (100mmX75mm) | 2.00 | Each |  | 235.00 | 470.00 | 500.00 | 1000.00 | 375.00 | 750.00 | 470.00 | ECS ENGINEERING PVT LTD
21.02 | 6 Module (200mmX75mm) | 4.00 | Each |  | 294.00 | 1176.00 | 750.00 | 3000.00 | 550.00 | 2200.00 | 1176.00 | ECS ENGINEERING PVT LTD
22.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
22.01 | 15/16 amp switch | 10.00 | Each |  | 194.00 | 1940.00 | 100.00 | 1000.00 | 180.00 | 1800.00 | 1000.00 | SUN POWER CONVERSION PVT LTD
22.02 | 6 pin 15/16 amp socket outlet | 10.00 | Each |  | 265.00 | 2650.00 | 150.00 | 1500.00 | 225.00 | 2250.00 | 1500.00 | SUN POWER CONVERSION PVT LTD
23.00 | Supply of 300 mm sweep, Heavy duty exhaust fan suitable for 1-Phase, 230V, 50Hz, with 1350-1400 RPM including provision of louver shutter,powder coated metalic body,motor with copper winding etc., complete as required. | 1.00 | Each |  | 3059.00 | 3059.00 | 2000.00 | 2000.00 | 3500.00 | 3500.00 | 2000.00 | SUN POWER CONVERSION PVT LTD
24.00 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. Up to 450 mm sweep | 1.00 | Each |  | 353.00 | 353.00 | 500.00 | 500.00 | 1000.00 | 1000.00 | 353.00 | ECS ENGINEERING PVT LTD
25.00 | Supply of 18W/20W LED (4 ft.) with LED lamp & batten for LED tube made of extruded aluminium/ poly carbonate housing with integrated electronic driver suitable for operation on 220V, 50 Hz AC supply etc. as per specification complete as required. | 10.00 | Each |  | 176.00 | 1760.00 | 200.00 | 2000.00 | 950.00 | 9500.00 | 1760.00 | ECS ENGINEERING PVT LTD
26.00 | Installation, testing and commissioning of pre-wired LED fittings of all type with all accessories including nut bolt washer and hanging/fixing arrangements if required directly on existing False ceiling / wall / surface/ ceiling/ etc. including electrical connection as per site requirement. | 10.00 | Each |  | 88.00 | 880.00 | 100.00 | 1000.00 | 200.00 | 2000.00 | 880.00 | ECS ENGINEERING PVT LTD
27.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 5.00 | Set |  | 9665.00 | 48325.00 | 6000.00 | 30000.00 | 12500.00 | 62500.00 | 30000.00 | SUN POWER CONVERSION PVT LTD
28.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm Dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 66.00 | Metre |  | 567.00 | 37422.00 | 775.00 | 51150.00 | 550.00 | 36300.00 | 36300.00 | Awasthi Electric Works
29.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 30.00 | Metre |  | 171.00 | 5130.00 | 150.00 | 4500.00 | 300.00 | 9000.00 | 4500.00 | SUN POWER CONVERSION PVT LTD
30.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2.00 | Set |  | 24059.00 | 48118.00 | 23000.00 | 46000.00 | 25500.00 | 51000.00 | 46000.00 | SUN POWER CONVERSION PVT LTD
31.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm Dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 36.00 | Metre |  | 2759.00 | 99324.00 | 2700.00 | 97200.00 | 2350.00 | 84600.00 | 84600.00 | Awasthi Electric Works
32.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 10.00 | Metre |  | 2012.00 | 20120.00 | 2100.00 | 21000.00 | 1950.00 | 19500.00 | 19500.00 | Awasthi Electric Works
33.00 | Supply, installation, testing and commissioning ISI marked (IS:15683) Fire Extinguisher, Carbon-di-oxide type capacity 4.5 Kg. Flat base including valve, discharge hose of not less than 10 mm dia, 1M long and complete in all respects including initial fill with CO2 gas conforming to IS:307-1966/IS 15222 and wall suspension braket complete as required. | 2.00 | Each |  | 3765.00 | 7530.00 | 6000.00 | 12000.00 | 8000.00 | 16000.00 | 7530.00 | ECS ENGINEERING PVT LTD
34.00 | Supply, installation, testing and commissioning of 6 kg ABC (Powder Type) Fire Extinguisher, Mild Steel Cylinders ISI marked fitted with pressure indicating gauge, internal tube, squeeze lever type valve fully charged with ABC 90 powder (Mono Ammonium Phosphate) pressured by Nitrogen complete in all respects including wall suspension bracket complete and conforming to IS:15683 as required. | 2.00 | Each |  | 2471.00 | 4942.00 | 5000.00 | 10000.00 | 4500.00 | 9000.00 | 4942.00 | ECS ENGINEERING PVT LTD
35.00 | All-inclusive comprehensive maintenance contract for 2 × 20 KVA UPS systems (For Item No. 01), including replacement of all spares (excluding batteries) as per OEM recommendations. The scope includes mandatory quarterly servicing and attending to breakdown calls within 24 hours, as and when required. (DLP shall be for Two year after the completion of work)
35.01 | AICMC charges for 1st year after DLP of 2 years @7.5% of item no.1 | 1.00 | Year |  | 54600.00 | 54600.00 | 44925.00 | 44925.00 | 26250.00 | 26250.00 | 26250.00 | Awasthi Electric Works
35.02 | AICMC charges for 2nd year after DLP of 2 years @8% of item no.1 | 1.00 | Year |  | 58240.00 | 58240.00 | 47920.00 | 47920.00 | 28000.00 | 28000.00 | 28000.00 | Awasthi Electric Works
35.03 | AICMC charges for 3rd year after DLP of 2 years @ 8.5% of item no.1 | 1.00 | Year |  | 61880.00 | 61880.00 | 50915.00 | 50915.00 | 29750.00 | 29750.00 | 29750.00 | Awasthi Electric Works
35.04 | AICMC charges for 4th year after DLP of 2 years @9% of item no.1 | 1.00 | Year |  | 65520.00 | 65520.00 | 53910.00 | 53910.00 | 31500.00 | 31500.00 | 31500.00 | Awasthi Electric Works
35.05 | AICMC charges for 5th year after DLP of 2 years @9.5% of item no.1 | 1.00 | Year |  | 69160.00 | 69160.00 | 56905.00 | 56905.00 | 33250.00 | 33250.00 | 33250.00 | Awasthi Electric Works
35.06 | AICMC charges for 6th year after DLP of 2 years @10% of item no.1 | 1.00 | Year |  | 72800.00 | 72800.00 | 59900.00 | 59900.00 | 35000.00 | 35000.00 | 35000.00 | Awasthi Electric Works
| Total in Figures |  |  |  |  | 2187001.00 |  | 1856490.00 |  | 1736750.00
Lowest Amount Quoted BY: Awasthi Electric Works(1736750.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of UPS for GLF facilities at Kanpur Airport (Inclusive of AICMC for 6 Years after DLP of 2 years) Tender ID: 2026_AAI_286949_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works (BID ID -1065751) | 1736750.00 | L1
| 2 | SUN POWER CONVERSION PVT LTD (BID ID -1065374) | 1856490.00 | L2
| 3 | ECS ENGINEERING PVT LTD (BID ID -1064251) | 2187001.00 | L3