## BoQ1
Government eProcurement System Created By: Mayur Mishra Created Date/Time: 29-Sep-2026 12:14 PM Tender Title: Reconfiguration and Misc repair work in AAI Residential colony at SVPI Airport, Ahmedabad. (Subhead- Electrical work 2026-27) Tender ID: 2026_AAI_287212_1
Tender Inviting Authority: Jt. Gen. Mgr. (Engg.-Elect.), AAI, Vadodara
Name of Work: Reconfiguration & Misc. repair work in AAI Residential colony at SVPI Airport, Ahmedabad. (Sub:- Electrical work 2026-27).
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Taral Electricals (GSTN-24ACMPR0280M1Z9) BID ID -1061060 |  | Yash Energy Pvt. Ltd (GSTN-24AAACY3771H1ZA) BID ID -1063907 |  | SAHA COMMERCIAL CONSTRUCTION (GSTN-19AASFS6288A1ZN) BID ID -1064909 |  | Techno Electricals (GSTN-24AAGFT9086M1ZG) BID ID -1065351 |  | Krishsons International Engineers And Consultants (I) Pvt. Ltd (GSTN-NA) BID ID -1065349 |  | Raksha Electricals (GSTN-NA) BID ID -1064001
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Supply, Installation, Testing & Commissioning of 9 Mtr. high mast system with its accessories. Mast shaft shall be in single sections, hot dip galvanised and suitable for wind velocity as per IS:875. It shall also include accessories for high mast including head frame, steel wire rope 6 mm dia (SS) with raising lowering system comprising, luminaries carriage suitable to install required 6 nos. of LED Light fixtures with its accessories in symmetrical arrangement, double drum winch, trailing cable, connector, junction box, lightening finial etc. The mast shall have an integral power tool motor, manual handle installed inside the base compartment for its operation. Work includes the installation of LED Flood Light luminiaries & LED type Aviation obstruction light & its wiring & connection complete and wiring material from junction box to individual luminaire & MCB in base compartment and following accessories etc. as required as per the enclosed specifications etc complete as required:- a) Providing & fixing of foundation bolts manufactured from special steel along with nuts, washers, anchor plate and common template (as per OEM standard). b) Construction of foundation including Soil testing, design & construction of RCC foundation suitable as per IS 875 for wind velocity withstand capacity with all materials and labour as per manufacturers recommendations including excavation, backfilling and concreting with grade not less than M20/M25 as per the approved Foundation design, along with fixing of templates, foundation bolts, trailing cable with plug and GT connector with all required accessories, terminations, connection etc. complete as required as per approved lighting design scheme, foundation drawing and tender specifications. | 3.00 | Job |  | 145013.00 | 435039.00 | 153700.00 | 461100.00 | 135000.00 | 405000.00 | 187500.00 | 562500.00 | 190000.00 | 570000.00 | 161200.00 | 483600.00 | 405000.00 | SAHA COMMERCIAL CONSTRUCTION
2.00 | Supply of Flood light LED fitting with minimum output of 14250 lumens and wattage not more than 150 W, suitable for 230V Single Phase AC supply, 50Hz, PF>0.95, CRI>70, CCT 4000K, Life of fitting not less than 50000 hrs complete as required. Luminaire should have high pressure die cast Alminium/standard alloy housing with surge protection system. Luminaire should have proper thermal management. Min IP protection should be IP65. The fixtures should comply with the specification available in respective Indian Standard Code for BIS. The fitting should have minimum 5 years warranty for complete luminaire including Driver & control gear etc. complete as required. (5 Years Warranty) | 20.00 | Each |  | 3954.00 | 79080.00 | 3410.00 | 68200.00 | 2950.00 | 59000.00 | 5300.00 | 106000.00 | 4800.00 | 96000.00 | 4500.00 | 90000.00 | 59000.00 | SAHA COMMERCIAL CONSTRUCTION
3.00 | Design, manufacture, supply, installation, testing and commissioning of outdoor totally enclosed double door feeder pillar for each 9 Mtr. High mast, made of 14 SWG CRCA sheet steel, totally enclosed, standing on a MS Angle frame suitably fixed on floor foundation, dust and vermin proof, powder coated painting, suitable for operation on 3 phase and neutral, 415 V, 50 Hz AC system with suitable connector for incoming and outgoing connection and interconnections including supply & installation of following items and as per specifications: Incomer: 01 No. 63 Amp., 4 Pole, MCB 10 KA, Digital Volt Meter with selector switch and control fuse: 1 Set Phase Indication Lights: 01 Set Bus Bars, RYBN (All same size) Outgoings: 32 A, 4 Pole C curve MCB-01 No. with 25 Amp. Contactor for HM lighting. 6-32 A, DP C curveMCB-03 Nos. Spare R&F DOL starter for operating power tool for 2HP motor Time Switch, Digital, 24 Hrs: 01 No. (All required hardware i.e. contactor, relays, control wiring etc. are included in this item.) | 3.00 | Job |  | 44915.00 | 134745.00 | 35200.00 | 105600.00 | 85000.00 | 255000.00 | 25000.00 | 75000.00 | 85000.00 | 255000.00 | 28000.00 | 84000.00 | 75000.00 | Techno Electricals
4.00 | Supply of single dome LED type aviation obstruction light luminair with lamp, fixtures, mounting clamp, nut bolt etc. complete as required. Bajaj make or as per the preferred make list of AAI. (5 Years Warranty) | 6.00 | Each |  | 4297.00 | 25782.00 | 2750.00 | 16500.00 | 6500.00 | 39000.00 | 4370.00 | 26220.00 | 3000.00 | 18000.00 | 2500.00 | 15000.00 | 15000.00 | Raksha Electricals
5.00 | Supply of 150 Watt LED type Road/ Street light with minimum protection level > IP 65, pressure die cast housing with epoxy power coated prismatic poly carbonate cover with individual LED lenses and complete assembly with LED, driver and accessories pre-wired up to terminal block i/c suitable mounting accessories etc. as required. [ Make: Bajaj, Model No.: ENXT P 180L WH PO TG SD or equivalent as approved by Engineer-in-Charge ] (5 Years Warranty) | 24.00 | Each |  | 3355.00 | 80520.00 | 3850.00 | 92400.00 | 3000.00 | 72000.00 | 5520.00 | 132480.00 | 4800.00 | 115200.00 | 2900.00 | 69600.00 | 69600.00 | Raksha Electricals
6.00 | Fixing of 150 watt LED street light/Post top fitting on pole (upto 25 mtr. height) including suitable clamping arrangement in existing poles, i/c connection with 1.5 Sq.mm PVC insulated copper conductor single core cable, testing and commissioning complete as required. | 22.00 | Each |  | 1881.00 | 41382.00 | 1100.00 | 24200.00 | 450.00 | 9900.00 | 800.00 | 17600.00 | 500.00 | 11000.00 | 300.00 | 6600.00 | 6600.00 | Raksha Electricals
7.00 | Supply of 45 Watt LED type Ring LED Post Top Lantern Fitting made in die cast aluminium bottom housing and spun aluminium top reflector with decorative clear acrylic diffuser and > IP 65 protection, opal diffuser available and complete assembly with LED, driver and accessories pre-wired up to terminal block i/c suitable mounting accessories etc. as required. Bajaj Cat Ref : BGCPNP 45W WW OP P(LED Post-Top "ARCHENAR")or equivalent as per AAI approved make list. (5 Years Warranty) | 33.00 | Each |  | 8290.00 | 273570.00 | 6380.00 | 210540.00 | 3750.00 | 123750.00 | 8000.00 | 264000.00 | 4800.00 | 158400.00 | 6620.00 | 218460.00 | 123750.00 | SAHA COMMERCIAL CONSTRUCTION
8.00 | Fixing of 45 watt LED type Ring Led Post Top Lantern Fitting on pole (upto 7 mtr. height) including suitable clamping arrangement in existing poles, i/c connection with 1.5 Sq.mm PVC insulated copper conductor single core cable, testing and commissioning complete as required. | 30.00 | Each |  | 1306.00 | 39180.00 | 660.00 | 19800.00 | 350.00 | 10500.00 | 500.00 | 15000.00 | 1400.00 | 42000.00 | 1050.00 | 31500.00 | 10500.00 | SAHA COMMERCIAL CONSTRUCTION
9.00 | PTTA TYPE PANEL Design, manufacture, supply, installation, testing and commissioning of outdoor compartmentalized type Panel 50 kA short circuit breaking capacity for perimeter lighting, having panel of suitable size, bus bars with SMC/DMC supports, made of 14 SWG CRCA sheet steel, totally enclosed, IP-65, free standing, floor / wall mounting, powder coated painting, suitable to the existing space, operation on 3 phase and neutral, 415V, 50 Hz AC system with bus bars, G.I flat Earth strip on both side , Removable gland plates at bottom with suitable size of predrilled holes for cables, cable interconnections, wiring, earthing, rotary handles & spreader links to all MCCBs, powder coated painting etc. with following items and installation on suitable channels /elevated concrete foundation as per site requirement/ directions of E-I-C. INCOMER MCCB of 125 Amps, 35 kA, 4 pole, microprocessor based release with Rotary operating mechanism, shunt trip, auxiliary contact etc. - 02 Nos. Indication Lamps, LED type, R.Y.B and breaker 'ON', 'OFF', 'TRIP' lamps- 02 Sets Digital Multifunctional meter suitable range for 3 phase, 4 wire with LED display and selector switch along with MCB of suitable ratings- 02 Sets, for 3 phase 4 wire with LED display and selector switch and cast resin CT ratio programmable and auto ranging along with 3 numbers of class 1.0, 15 VA suitable range CTs -02 Sets.. BUSCOUPLER MCCB of 125 Amps, 35 kA, 4 pole, microprocessor based release with Rotary operating mechanism, shunt trip, auxiliary contact etc., - 01 No. Indication Lamps, LED type, R.Y.B and breaker 'ON', 'OFF', 'TRIP' lamps- 01 Set mechanical interlocking arrangement between 2 nos. 125 Amp incomer, -1 set BUSBAR One set of 400 Amp TPN aluminium bus bars of 35 KA capacity. OUTGOING 4 Pole, 35 kA, 100 Amp MCCB - 2 No. and 63 Amp MCCB - 4 No. with extended terminal with suitable rating, direct rotary handle etc as required. Indication Lamps, LED type, R.Y.B and breaker 'ON', 'OFF', 'TRIP' lamps- 06 Set | 1.00 | Job |  | 683144.00 | 683144.00 | 462000.00 | 462000.00 | 295000.00 | 295000.00 | 222525.00 | 222525.00 | 400000.00 | 400000.00 | 325000.00 | 325000.00 | 222525.00 | Techno Electricals
10.00 | Supply of following Size 1.1 KV grade alumuninum conductor XLPE insulated and PVC sheathed armoured power cable as per IS 7098:1988 (Part-I) with upto date amendments. A)4 Core X 16 Sq.mm | 600.00 | Mtr |  | 163.00 | 97800.00 | 149.00 | 89400.00 | 205.00 | 123000.00 | 180.00 | 108000.00 | 180.00 | 108000.00 | 350.00 | 210000.00 | 89400.00 | Yash Energy Pvt. Ltd
11.00 | Laying of one number PVC/ XLPE insulated and PVC sheathed cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe/ HDPE Pipe as required. A) Upto 35 Sq.mm | 570.00 | Mtr |  | 22.00 | 12540.00 | 44.00 | 25080.00 | 45.00 | 25650.00 | 28.00 | 15960.00 | 35.00 | 19950.00 | 5.00 | 2850.00 | 2850.00 | Raksha Electricals
12.00 | Laying of one number PVC/ XLPE insulated and PVC sheathed power cable of 1.1 KV grade of following size in masonnary open duct etc as required. A) Upto 35 Sq.mm | 30.00 | Mtr |  | 22.00 | 660.00 | 39.00 | 1170.00 | 45.00 | 1350.00 | 28.00 | 840.00 | 20.00 | 600.00 | 15.00 | 450.00 | 450.00 | Raksha Electricals
13.00 | Supply of following dia DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. complete as required. A) 50 mm dia (OD-50 mm & ID-38 mm nominal ) | 600.00 | Mtr |  | 53.00 | 31800.00 | 52.00 | 31200.00 | 105.00 | 63000.00 | 75.00 | 45000.00 | 60.00 | 36000.00 | 40.00 | 24000.00 | 24000.00 | Raksha Electricals
14.00 | Laying of 50 mm dia (OD-50 mm & ID-38 mm nominal) DWC HDPE pipe along with all accessories like socket, bend, couplers etc complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) i/c excavation and refilling the trench but excluding sand cushioning and protective covering etc conforming to IS 14930, Part II complete as required. | 600.00 | Mtr |  | 96.00 | 57600.00 | 132.00 | 79200.00 | 115.00 | 69000.00 | 115.00 | 69000.00 | 80.00 | 48000.00 | 120.00 | 72000.00 | 48000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
15.00 | Providing and Laying of following dia 'B' class GI Pipe including excavation of hard / soft soil complete with threading and alignment of pipe, bituminous road/concrete surface cutting for laying the pipe and making good the same with 1:2:4 cement concrete etc. as required. A) 100 mm dia 'B' class GI Pipe | 50.00 | Mtr |  | 1417.00 | 70850.00 | 1540.00 | 77000.00 | 1095.00 | 54750.00 | 1200.00 | 60000.00 | 1600.00 | 80000.00 | 1000.00 | 50000.00 | 50000.00 | Raksha Electricals
16.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. A) 4 X 16 Sq. mm | 10.00 | Set |  | 395.00 | 3950.00 | 594.00 | 5940.00 | 450.00 | 4500.00 | 375.00 | 3750.00 | 400.00 | 4000.00 | 300.00 | 3000.00 | 3000.00 | Raksha Electricals
17.00 | Supply of 20 watt surface and wall mounted LED batten (4 ft) with polycarbonate housing & integrated electronic driver i/c pre-wired, complete with all accessories and tube etc. directly on ceiling/ wall etc. as required. (5 Years Warranty) | 227.00 | Each |  | 266.00 | 60382.00 | 121.00 | 27467.00 | 225.00 | 51075.00 | 225.00 | 51075.00 | 140.00 | 31780.00 | 170.00 | 38590.00 | 27467.00 | Yash Energy Pvt. Ltd
18.00 | Installation, testing and commissioning of pre-wired, LED fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 Sq.mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 216.00 | Each |  | 95.00 | 20520.00 | 110.00 | 23760.00 | 75.00 | 16200.00 | 200.00 | 43200.00 | 60.00 | 12960.00 | 40.00 | 8640.00 | 8640.00 | Raksha Electricals
19.00 | Supply and fixing call bell / buzzer including bell switch suitable for single phase,230 V complete as req. | 38.00 | Each |  | 444.00 | 16872.00 | 220.00 | 8360.00 | 225.00 | 8550.00 | 275.00 | 10450.00 | 250.00 | 9500.00 | 230.00 | 8740.00 | 8360.00 | Yash Energy Pvt. Ltd
20.00 | Supply and fixing of 300 mm sweep, 900 rpm heavy duty exhaust fan i/c fixing of louvers/shutters with frame for exhaust fan suitable for operation on 230 /240 volts, 50 Hz Single phase ,A.C. supply complete as req. | 36.00 | Each |  | 3105.00 | 111780.00 | 3300.00 | 118800.00 | 2250.00 | 81000.00 | 5000.00 | 180000.00 | 3350.00 | 120600.00 | 1750.00 | 63000.00 | 63000.00 | Raksha Electricals
21.00 | Supply of BLDC celling Fan without remote control, 1200 mm sweep, BEE 5 star rated suitable for 230 volt, with 30 cm down rod and suitable for operation with regulator for speed control, other accessories, canopies, etc. as required. (2 Years Warranty) | 137.00 | Each |  | 2662.00 | 364694.00 | 2035.00 | 278795.00 | 3150.00 | 431550.00 | 2500.00 | 342500.00 | 3300.00 | 452100.00 | 2980.00 | 408260.00 | 278795.00 | Yash Energy Pvt. Ltd
22.00 | Installation, testing and commissioning of BLDC ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 Sq.mm FRLSH PVC insulated, copper conductor, single core cable etc. as required. | 130.00 | Each |  | 250.00 | 32500.00 | 110.00 | 14300.00 | 125.00 | 16250.00 | 255.00 | 33150.00 | 125.00 | 16250.00 | 130.00 | 16900.00 | 14300.00 | Yash Energy Pvt. Ltd
23.00 | Supply of 45 Watt LED type Road/ Street light with minimum protection level IP 66, pressure die cast housing with epoxy power coated prismatic poly carbonate cover with individual LED lenses and complete assembly with LED, driver and accessories pre-wired up to terminal block i/c suitable mounting accessories etc. as required. (5 Years Warranty) | 121.00 | Each |  | 1187.00 | 143627.00 | 1100.00 | 133100.00 | 1150.00 | 139150.00 | 1675.00 | 202675.00 | 1200.00 | 145200.00 | 3000.00 | 363000.00 | 133100.00 | Yash Energy Pvt. Ltd
24.00 | Fixing of LED street light fitting on pole / wall including bending the suitable size GI pipe to the required shape, iron clamps with nuts, bolts and washer, painting the flat iron with primer and finish paint including connection with 1.5 Sq.mm PVC insulated copper conductor single core cable, testing and commissioning complete as required. | 115.00 | Each |  | 762.00 | 87630.00 | 275.00 | 31625.00 | 350.00 | 40250.00 | 300.00 | 34500.00 | 150.00 | 17250.00 | 145.00 | 16675.00 | 16675.00 | Raksha Electricals
25.00 | Supply of Aluminium wall supporting extension ladder made out of C section and steps of Aluminium corrugated tubing fitted with heavy duty safety lock, 12 feet, pully, rope and rubber pads at bottom and upper ends. | 1.00 | Each |  | 14399.00 | 14399.00 | 11660.00 | 11660.00 | 10500.00 | 10500.00 | 27000.00 | 27000.00 | 12000.00 | 12000.00 | 10000.00 | 10000.00 | 10000.00 | Raksha Electricals
26.00 | Supply and Installation of Astro Mini time switch suitable for single phase 240V AC for lighting control based on sunrise/sunset timings by lattitude/longititude settings. | 2.00 | Each |  | 5600.00 | 11200.00 | 1540.00 | 3080.00 | 2500.00 | 5000.00 | 4500.00 | 9000.00 | 8285.00 | 16570.00 | 1500.00 | 3000.00 | 3000.00 | Raksha Electricals
27.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required.(CPWD DSR-2025 item 5.2) | 13.00 | Job |  | 6876.00 | 89388.00 | 7150.00 | 92950.00 | 4500.00 | 58500.00 | 6500.00 | 84500.00 | 8000.00 | 104000.00 | 5000.00 | 65000.00 | 58500.00 | SAHA COMMERCIAL CONSTRUCTION
28.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. (CPWD DSR-2025 item 5.11) | 100.00 | Mtr. |  | 507.00 | 50700.00 | 561.00 | 56100.00 | 350.00 | 35000.00 | 655.00 | 65500.00 | 749.00 | 74900.00 | 400.00 | 40000.00 | 35000.00 | SAHA COMMERCIAL CONSTRUCTION
29.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required.(CPWD DSR-2025 item 5.15) | 50.00 | Mtr. |  | 142.00 | 7100.00 | 165.00 | 8250.00 | 95.00 | 4750.00 | 200.00 | 10000.00 | 275.00 | 13750.00 | 125.00 | 6250.00 | 4750.00 | SAHA COMMERCIAL CONSTRUCTION
30.00 | SITC of single phase neutral surge protection device (SPD), Type-2, 2 model, 1P+N with inbuilt MCB having maximum recharge current 40KA (10/350 us), impulse current 8KA with protection level of 0-1.5kv including all accessories confirming to IEC 61643-11, Cat. No. DHSA2NAN40320, Make: Havells or equivalent as per AAI approved make list. | 38.00 | Each |  | 1630.00 | 61940.00 | 1595.00 | 60610.00 | 1250.00 | 47500.00 | 1200.00 | 45600.00 | 3600.00 | 136800.00 | 1500.00 | 57000.00 | 45600.00 | Techno Electricals
31.00 | Supply of 1.5 TR Eco-friendly refrigerant Split Inverter type Air Conditioner of having nominal cooling capacity 1.5/4500, 5 Star BEE rating, conforming to IS:1391 with copper coil, 10ft copper pipe, suitable copper cable, 5 years warranty on compressor and 1 year warranty on machine etc. complete as required.​ | 14.00 | Each |  | 37484.00 | 524776.00 | 39600.00 | 554400.00 | 42500.00 | 595000.00 | 37500.00 | 525000.00 | 45000.00 | 630000.00 | 38000.00 | 532000.00 | 524776.00 | Taral Electricals
32.00 | Installation, Testing & Commissioning of 1.5 TR Eco-friendly refrigerant Split Inverter Air Conditioner etc. complete as required. | 14.00 | Each |  | 1220.00 | 17080.00 | 1650.00 | 23100.00 | 2250.00 | 31500.00 | 3000.00 | 42000.00 | 500.00 | 7000.00 | 1500.00 | 21000.00 | 7000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
33.00 | Supplying and fixing of floor mounted MS angle Stand (1.5 feet height) suitable for mounting 1.5 TR split AC outdoor unit including painting etc complete as required. | 14.00 | Each |  | 555.00 | 7770.00 | 550.00 | 7700.00 | 350.00 | 4900.00 | 1255.00 | 17570.00 | 500.00 | 7000.00 | 550.00 | 7700.00 | 4900.00 | SAHA COMMERCIAL CONSTRUCTION
34.00 | Providing of extra refrigerant piping, cabling (More than standard length), insulating with foam between indoor and outdoor units etc. as required. | 100.00 | Mtr. |  | 1187.00 | 118700.00 | 330.00 | 33000.00 | 1050.00 | 105000.00 | 1000.00 | 100000.00 | 700.00 | 70000.00 | 430.00 | 43000.00 | 33000.00 | Yash Energy Pvt. Ltd
35.00 | Providing and fixing of extra drain CPVC / UPVC pipe for condensate water from indoor unit to nearest drain point etc. as required. | 50.00 | Mtr. |  | 94.00 | 4700.00 | 55.00 | 2750.00 | 150.00 | 7500.00 | 175.00 | 8750.00 | 100.00 | 5000.00 | 50.00 | 2500.00 | 2500.00 | Raksha Electricals
36.00 | Dismantling of existing 1.5 Ton/ 2 Ton Split AC Units with all accessories including loading and unloading complete etc .as required upto AAI store. | 14.00 | Each |  | 998.00 | 13972.00 | 220.00 | 3080.00 | 350.00 | 4900.00 | 1700.00 | 23800.00 | 300.00 | 4200.00 | 650.00 | 9100.00 | 3080.00 | Yash Energy Pvt. Ltd
37.00 | Supply, Installation, Testing & Commissioning of fully stainless steel storage type water cooler of capacity 40/80 Liter (40 Ltr/Hr, cooling capacity & 80 Ltr storage capacity). Suitable for single phase 230V ± 10, 50Hz AC supply as per OEM specification with inlet hose connection inlet float valce, 2 nos. outlet faucet, drain pan with piping up to floor trap, suitable MS angle stand etc. complete in all respect as per approved makes required | 4.00 | Each |  | 34989.00 | 139956.00 | 36750.00 | 147000.00 | 40000.00 | 160000.00 | 38000.00 | 152000.00 | 37000.00 | 148000.00 | 32500.00 | 130000.00 | 130000.00 | Raksha Electricals
38.00 | Supply, installation, testing and commissioning of Commercial wall mounted type RO + UV Water Purifier with at least 50 liter per hour capacity, with TDS adjustor, fully automatic with auto cut off with operation of 230V, 50Hz, Single phase AC electric supply, portable water purification system etc. complete with inlet pipe and fittings as per approved makes required | 4.00 | Each |  | 35932.00 | 143728.00 | 68250.00 | 273000.00 | 42500.00 | 170000.00 | 28000.00 | 112000.00 | 43000.00 | 172000.00 | 41200.00 | 164800.00 | 112000.00 | Techno Electricals
39.00 | Supply, installation, testing and commissioning of wall mounted type RO + UV + UF Water Purifier with at least 20 liter per hour capacity with inbuilt ABS food grade water tank of at least 8 liter water storage capacity, fully automatic with auto cut off with operation of 230V, 50Hz, Single phase AC electric supply etc. complete with inlet pipe and fittings as per approved makes required | 7.00 | Each |  | 17966.00 | 125762.00 | 44625.00 | 312375.00 | 15500.00 | 108500.00 | 17500.00 | 122500.00 | 20000.00 | 140000.00 | 18500.00 | 129500.00 | 108500.00 | SAHA COMMERCIAL CONSTRUCTION
| Total in Figures |  |  |  |  | 4236818.00 |  | 3994592.00 |  | 3742975.00 |  | 3966645.00 |  | 4309010.00 |  | 3830715.00
Lowest Amount Quoted BY: SAHA COMMERCIAL CONSTRUCTION(3742975.00)

## BOQ Summary
BOQ Summary Details Tender Title: Reconfiguration and Misc repair work in AAI Residential colony at SVPI Airport, Ahmedabad. (Subhead- Electrical work 2026-27) Tender ID: 2026_AAI_287212_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SAHA COMMERCIAL CONSTRUCTION (BID ID -1064909) | 3742975.00 | L1
| 2 | Raksha Electricals (BID ID -1064001) | 3830715.00 | L2
| 3 | Techno Electricals (BID ID -1065351) | 3966645.00 | L3
| 4 | Yash Energy Pvt. Ltd (BID ID -1063907) | 3994592.00 | L4
| 5 | Taral Electricals (BID ID -1061060) | 4236818.00 | L5
| 6 | Krishsons International Engineers And Consultants (I) Pvt. Ltd (BID ID -1065349) | 4309010.00 | L6