## BoQ1
Government eProcurement System Created By: Prakash Chandra Created Date/Time: 23-Sep-2026 09:58 AM Tender Title: Modification of existing Terminal Building and replacement of false ceiling at Gaya Airport. SH Internal Electrical Works Tender ID: 2026_AAI_288204_1
Tender Inviting Authority: <SM ( Engg. Elect), AAI, Gaya Airport, Gaya>
Name of Work: <Modification of existing Terminal Building and replacement of false ceiling at Gaya Airport. SH: Internal Electrical Works.>
Contract No: <2026_AAI_288204_1>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | TARUN ELECTRICALS (GSTN-08ANCPM5157F1Z0) BID ID -1060898 |  | Instapower Ltd (GSTN-05AAACI9712L1ZG) BID ID -1066608 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -1067747 |  | M/S B. PRASAD & COMPANY (GSTN-NA) BID ID -1061234 |  | B L ENTERPRISES (GSTN-NA) BID ID -1067674
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of 36 W(+/-10%) linear type LED luminaire (4 ft) suitable for mounting on false ceiling, made of extruded aluminum housing complying construction requirements as per IS:10322 with Driver efficiency>85%,internal surge protection of 2.5 KV with Short & Open circuit protection, THD < 10%, P. F.≥0.95, IP20, IK02, CRI ≥80, UGR(Unified Glare Rating)<19, Flicker free, (flicker should be below 5 %),life time (LED, Driver & electrical circuitry), of minimum 50000 Burning Hours with , 70% of initial Lumen maintained till life ends ,CCT 3000°K / 4000°K /5700°K/6500°K (As per ANSI Bin), SDCM(Standard Deviation Colour Matching)<3,Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard. Manufactures Word Mark/ Name Engraved/ Embossing/ Screen printing on housing (Stickers shall not be acceptable) complete in all respect i/c external connections with 1.5 sq.mm FRLS/HFFR, PVC insulated copper conductor single core cable and earthing etc. as required with Minimum 5 year OEM warranty. System lumen efficacy ≥135 lm/Watt output. LM79 & LM80 Test report and all testing required for LED fixtures as per BIS shall be submitted with technical datasheets for approval from EIC. Shape size and CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management:heat sink of aluminium housing such that LED junction temperature shall not rise above 90°C).Quote should include preparation & submission of lighting design , illumination calculations using industry-standard lighting design software, preparation of photometric layouts, lux-level calculations, uniformity calculations, glare assessment, lighting power density (LPD) calculations, reflected ceiling plans (RCP) complete as per instructions of Engineer-In-Charge. | 720.00 | Each | 263.00 | 3500.00 | 2520000.00 | 3321.00 | 2391120.00 | 4000.00 | 2880000.00 | 6900.00 | 4968000.00 | 5500.00 | 3960000.00 | 2391120.00 | Instapower Ltd
2.00 | Supply of 45 W(+/-10%) linear type LED luminaire(8 ft) suitable for mounting on false ceiling, made of extruded aluminum housing complying construction requirements as per IS:10322 with Driver efficiency >85%, internal surge protection of 2.5 KV with Short & Open circuit protection, THD < 10%, P. F.≥0.95, IP20, IK02, CRI ≥80, UGR (Unified Glare Rating) < 19, Flicker free, (flicker should be below 5 %), life time (LED, Driver & electrical circuitry), of minimum 50000 Burning Hours with , 70% of initial Lumen maintained till life ends ,CCT 3000°K / 4000°K / 5700°K /6500°K (As per ANSI Bin), SDCM(Standard Deviation Colour Matching)<3,Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard. Manufactures Word Mark/ Name Engraved/ Embossing/ Screen printing on housing(Stickers shall not be acceptable). complete in all respect i/c external connections with 1.5 sq.mm FRLS/HFFR, PVC insulated copper conductor single core cable and earthing etc. as required with Minimum 5 year OEM warranty. System lumen efficacy ≥135 lm/Watt output .LM79 & LM80 Test report and all testing required for LED fixtures as per BIS shall be submitted with technical datasheets for approval from EIC. Shape size and CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminium housing such that LED junction temperature shall not rise above 90°C).Quote should include preparation & submission of lighting design , illumination calculations using industry-standard lighting design software, preparation of photometric layouts, lux-level calculations, uniformity calculations, glare assessment, lighting power density (LPD) calculations, reflected ceiling plans (RCP) complete as per instructions of Engineer-In-Charge. | 200.00 | Each | 263.00 | 4000.00 | 800000.00 | 6765.00 | 1353000.00 | 7200.00 | 1440000.00 | 8400.00 | 1680000.00 | 7600.00 | 1520000.00 | 800000.00 | TARUN ELECTRICALS
3.00 | Supply 600mm x 600 mm 36 W(+/-10%) LED recessed mounted panel suitable for mounting on false ceiling, made of extruded aluminum housing complying construction requirements as per IS:10322 with Driver efficiency >85%,internal surge protection of 2.5 KV with Short & Open circuit protection, THD < 10%, P. F.≥0.95, IP20, IK02, CRI ≥80, UGR (Unified Glare Rating) < 19, Flicker free, (flicker should be below 5 %), life time (LED, Driver & electrical circuitry), of minimum 50000 Burning Hours with , 70% of initial Lumen maintained till life ends ,CCT 3000°K / 4000°K / 5700°K/6500°K (As per ANSI Bin), SDCM(Standard Deviation Colour Matching)<3,Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard. Manufactures Word Mark/ Name Engraved/Embossing/Screen printing on housing(Stickers shall not be acceptable) complete in all respect i/c external connections with 1.5 sq.mm FRLS/HFFR, PVC insulated copper conductor single core cable and earthing etc. as required with Minimum 5 year OEM warranty. System lumen efficacy≥135 lm/Watt output . LM79 & LM80 Test report and all testing required for LED fixtures as per BIS shall be submitted with technical datasheets for approval from EIC. Shape size and CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminium housing such that LED junction temperature shall not rise above 90°C).Quote should include preparation & submission of lighting design , illumination calculations using industry-standard lighting design software, preparation of photometric layouts, lux-level calculations, uniformity calculations, glare assessment, lighting power density (LPD) calculations, reflected ceiling plans (RCP) complete as per instructions of Engineer-In-Charge. | 250.00 | Each | 263.00 | 4000.00 | 1000000.00 | 3321.00 | 830250.00 | 2450.00 | 612500.00 | 3400.00 | 850000.00 | 1900.00 | 475000.00 | 475000.00 | B L ENTERPRISES
4.00 | Supply of 24 W(+/-10%) deep recessed LED Downlighter fittings suitable for mounting on false ceiling with housing complying construction requirements as per IS:10322 with Driver efficiency >85%, internal surge protection of 2.5 KV with Short & Open circuit protection, THD < 10%, P. F.≥0.95, IP20, IK02, CRI ≥80, UGR (Unified Glare Rating) < 19, Flicker free, (flicker should be below 5 %), life time (LED, Driver & electrical circuitry), of minimum 50000 Burning Hours with , 70% of initial Lumen maintained till life ends ,CCT 3000°K / 4000°K / 5700°K /6500°K (As per ANSI Bin), SDCM(Standard Deviation Colour Matching)<3,Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard. Manufactures Word Mark/ Name Engraved/Embossing/Screen printing on housing(Stickers shall not be acceptable) complete in all respect i/c external connections with 1.5 sq.mm FRLS/HFFR, PVC insulated copper conductor single core cable and earthing etc. as required with Minimum 5 year OEM warranty.System lumen efficacy≥120 lm/Watt output.LM79 & LM80 Test report and all testing required for LED fixtures as per BIS shall be submitted with technical datasheets for approval from EIC. Shape size, CCT and Beam Angle shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminium housing such that LED junction temperature shall not rise above 90°C).Quote should include preparation & submission of lighting design , illumination calculations using industry-standard lighting design software, preparation of photometric layouts, lux-level calculations, uniformity calculations, glare assessment, lighting power density (LPD) calculations, reflected ceiling plans (RCP) complete as per instructions of Engineer-In-Charge. | 200.00 | Each | 263.00 | 3500.00 | 700000.00 | 1168.50 | 233700.00 | 1500.00 | 300000.00 | 1800.00 | 360000.00 | 1500.00 | 300000.00 | 233700.00 | Instapower Ltd
5.00 | Supply of 80 W(+/-10%) LED Surface mounted LED High Bay Light fittings powder coated pressure die cast aluminium body with separate driver as per the requirement with Driver efficiency>85%,internal surge protection of 5 KV L,N,E as per IEC 61000-4-5,THD < 10% as per IEC 61000-3-2, P. F.≥0.95, IP-66,IK-10, CRI>70, under voltage and over voltage protection,EMI-EMC as per CISPR-15, lenses for beam angle 30 deg-120 deg, suitable tiltable fitting, life time (LED, Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report, CCT 3000°K / 4000°K / 5700°K /6500°K (As per ANSI Bin) , SDCM(Standard Deviation Colour Matching) <5, Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard complete in all respect i/c external connections with 1.5 sq.mm FRLS/HFFR,PVC insulated copper conductor single core cable and earthing etc. as required with Minimum 5 year OEM warranty. System lumen efficacy ≥135 lm/Watt output. LM79 & LM80 Test report and all testing required for LED fixtures as per BIS shall be submitted. Shape size,beam angle and CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminium housing such that LED junction temperature shall not rise above 90°C).Quote should include preparation & submission of lighting design , illumination calculations using industry-standard lighting design software, preparation of photometric layouts, lux-level calculations, uniformity calculations, glare assessment, lighting power density (LPD) calculations, reflected ceiling plans (RCP) complete as per instructions of Engineer-In-Charge. | 60.00 | Each | 263.00 | 3000.00 | 180000.00 | 2706.00 | 162360.00 | 3700.00 | 222000.00 | 12000.00 | 720000.00 | 4200.00 | 252000.00 | 162360.00 | Instapower Ltd
6.00 | Supply of 120 W (+/-10%) LED Streetlight fitting powder coated pressure die cast aluminium body with separate driver as per the requirement with Driver efficiency>85%,internal surge protection of 5 KV L,N,E as per IEC 61000-4-5,THD < 10% as per IEC 61000-3-2, P. F.≥0.95, IP-66,IK-10, CRI>70, under voltage and over voltage protection,EMI-EMC as per CISPR-15, lenses for beam angle 30 deg-120 deg, suitable tiltable fitting, life time (LED, Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report, CCT 3000°K / 4000°K / 5700°K /6500°K (As per ANSI Bin) , SDCM(Standard Deviation Colour Matching) <5, Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard complete in all respect i/c external connections with 1.5 sq.mm FRLS/HFFR,PVC insulated copper conductor single core cable and earthing etc. as required with Minimum 5 year OEM warranty. System lumen efficacy≥135 lm/Watt output. LM79 & LM80 Test report and all testing required for LED fixtures as per BIS shall be submitted. Shape size,beam angle and CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminium housing such that LED junction temperature shall not rise above 90°C).Quote should include preparation & submission of lighting design , illumination calculations using industry-standard lighting design software, preparation of photometric layouts, lux-level calculations, uniformity calculations, glare assessment, lighting power density (LPD) calculations, complete as per instructions of Engineer-In-Charge. | 50.00 | Each | 263.00 | 3500.00 | 175000.00 | 3936.00 | 196800.00 | 3750.00 | 187500.00 | 11500.00 | 575000.00 | 4600.00 | 230000.00 | 175000.00 | TARUN ELECTRICALS
7.00 | Suppy of following size PVC insulated and PVC Sheathed XLPE armoured Aluminium conductor cable of 1.1KV grade confirming to IS:7098(Part-1),1988 with up to date amendments complete as required.
7.10 | 4C x 4 Sq.mm | 1000.00 | Metre | 263.00 | 180.00 | 180000.00 | 252.15 | 252150.00 | 125.00 | 125000.00 | 145.00 | 145000.00 | 190.00 | 190000.00 | 125000.00 | Awasthi Electric Works
7.20 | 4C x 10 Sq.mm | 750.00 | Metre | 263.00 | 300.00 | 225000.00 | 399.75 | 299812.50 | 170.00 | 127500.00 | 170.00 | 127500.00 | 300.00 | 225000.00 | 127500.00 | M/S B. PRASAD & COMPANY, Awasthi Electric Works
7.30 | 4C x 25 Sq.mm | 500.00 | Metre | 263.00 | 400.00 | 200000.00 | 543.66 | 271830.00 | 250.00 | 125000.00 | 300.00 | 150000.00 | 400.00 | 200000.00 | 125000.00 | Awasthi Electric Works
8.00 | Installation,Testing and Commissioning of pre wired recess/surface mounted LED lights of various wattage complete with all accessories for indoor/outdoor locations including connection with 1.5 sq mm FRLS PVC insulated,copper conductor,single core cable and earthing etc at height of upto 20 mtrs. Quote should include hiring charges of boom/scissor lifts, safety helmets, safety harness etc complete as required. | 1480.00 | Each | 263.00 | 900.00 | 1332000.00 | 1950.00 | 2886000.00 | 1000.00 | 1480000.00 | 300.00 | 444000.00 | 100.00 | 148000.00 | 148000.00 | B L ENTERPRISES
9.00 | Dismantling of existing light fixtures & connected wiring/conduits, all items related to light fittings (as required) as per Direction of Engineer In Charge and making list of items and handing over to Department i/c shifting the materials from Terminal Building to Electrical store (distance upto 1000 mtrs) as per instructions of Engineer-In-Charge complete as required. | 900.00 | Each | 263.00 | 500.00 | 450000.00 | 260.00 | 234000.00 | 1000.00 | 900000.00 | 10.00 | 9000.00 | 50.00 | 45000.00 | 9000.00 | M/S B. PRASAD & COMPANY
10.00 | Execution of works as per CPWD Delhi Schedule of Rates (E&M)-2025 as and when required for an amount of Rs.40,00,000/-.(Rate shall be quoted in the Indian rupees only), payment of DSR item will be released on the basis of percentage calculation of quoted amount and fixed amount of Rs.40,00,000/- as clarified below. For example if desired to quote 5% above on DSR E&M) 2025 rates, the rate column shall be filled as Rs. 42,00,000.00. If desired to quote 5% below on DSR (E&M) 2025 rates, the rate column shall be filled as Rs. 38,00,000/-.Payment methodology shall be as detailed in SCC. | 1.00 | Job | 263.00 | 4600000.00 | 4600000.00 | 5500000.00 | 5500000.00 | 3600000.00 | 3600000.00 | 3200000.00 | 3200000.00 | 3000000.00 | 3000000.00 | 3000000.00 | B L ENTERPRISES
| Total in Figures |  |  |  |  | 12362000.00 |  | 14611022.50 |  | 11999500.00 |  | 13228500.00 |  | 10545000.00
Lowest Amount Quoted BY: B L ENTERPRISES(10545000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Modification of existing Terminal Building and replacement of false ceiling at Gaya Airport. SH Internal Electrical Works Tender ID: 2026_AAI_288204_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | B L ENTERPRISES (BID ID -1067674) | 10545000.00 | L1
| 2 | Awasthi Electric Works (BID ID -1067747) | 11999500.00 | L2
| 3 | TARUN ELECTRICALS (BID ID -1060898) | 12362000.00 | L3
| 4 | M/S B. PRASAD & COMPANY (BID ID -1061234) | 13228500.00 | L4
| 5 | Instapower Ltd (BID ID -1066608) | 14611022.50 | L5