## BoQ1
Government eProcurement System Created By: LAKSHMI NARAYANA CHODAVARAPU Created Date/Time: 17-Sep-2026 04:28 PM Tender Title: Beautification of approach road to new terminal building with landscaping, hardscaping, horticulture and sculpture works and associated lighting works at Vijayawada International Airport. SH ELECTRICAL WORKS Tender ID: 2026_AAI_288828_1
Tender Inviting Authority:Sr. Manager (Engg-E), Airports Authority of India, Vijayawada International Airport.
Name of Work: Beautification of approach road to new terminal building with landscaping, hardscaping, horticulture and sculpture works and associated lighting works at Vijayawada International Airport". SH: ELECTRICAL WORKS.
Contract No: 2026_AAI_288828_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Balaji Engineering (GSTN-33ADGPV2628A1ZV) BID ID -1065447 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -1065539 |  | Instapower Ltd (GSTN-05AAACI9712L1ZG) BID ID -1066595 |  | epic enterprise (GSTN-NA) BID ID -1065354 |  | SYNERGY LIGHTING SOLUTIONS (GSTN-NA) BID ID -1065348
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of minimum 150W surface mounted LED Flood projector with delivered Luminous flux of minimum 80lm/W. FIxture should have body in die?cast aluminium/extrusion and glass sealed optical chamber. The luminaire shall have a rated system lifetime of 50,000 burning hours at L70. The luminaire should have a colour temperature of 3000K and CRI > 70 and IK10 with IEC 60598 certification. The luminaire shall meet IP66 with THD < 10% and PF > 0.9. Operating Voltage 140-270VAC,The Surge Protection to be provided conforming to relevant IS standards/IEC 61643-II Class-2 , Quality Standard ISO 9001, Environmental Standard ISO 14001, Luminaire shall have dual optics with primary optics distribution of 120 degree or higher and secondary optics as per site/boq requirement. All the luminaires shall have LM-79 , the testing facility to generate the LM-79 should be at vendor (Not Sub Vendor) address during production and LM-80 of LED shoulde be available. Radiation Emission Measurement as per CISPR.15:2018, Conducted Emission Measurement as per CISPR.15:2018, Output voltage ripple should be within 3%, Full Load Efficiency of the driver ≥ 85%. The total power consumption should not exceed 250W (including driver). Luminaires and driver both shall be BIS certified individually. Heat sink used should be extruded Aluminum or Pressure Die-Cast Aluminum having high conductivity preferably ADC 12 or LM6. An extruded silicon loop gasket shall be provided in the lantern body to ensure a weather proof seal between the cover and the metal housing to exclude the entry of dust, water, insects, etc. Luminaire should conform to degree of protection of IP 65 or above. Mini IP68 water proof Gel box connector with PP Glue to be provided. Fixture should have beam distribution of 60° , 90° , 120° or as per consultant. Fixture should be compatible with accessory like Baffle as well as snoot for minimum glare.T he product shall be complete with all factory-fitted accessories, mounting hardware, weatherproof cable entries and connectors required for proper installation including suitable foundation and operation. The manufacturers name/logo should be engraved/embossed on the housing/body or Name/Logo on aluminum plate labels or Name/logo printed on housing/body etc. complete as required and as approved by Engineer In Charge. Location: SCULPTURE / STATUE | 60.00 | Each |  | 46000.00 | 2760000.00 | 40000.00 | 2400000.00 | 7485.00 | 449100.00 | 7625.00 | 457500.00 | 15000.00 | 900000.00 | 449100.00 | Instapower Ltd
2.00 | SITC of minimum 15W( Lamp Degree 24⁰ ) surface mounted LED spot projector with delivered Luminous flux of minimum 35 lm/W. FIxture should have body in die-cast aluminium/extrusion and glass sealed optical chamber. The luminaire shall have a rated system lifetime of 50,000 burning hours at L70. The luminaire should have a colour temperature of RGBW and CRI > 70 and IK10 with IEC 60598 certification. The luminaire shall meet IP66 with THD < 10% and PF > 0.9. Operating Voltage 140-270VAC,The Surge Protection to be provided conforming to relevant IS standards/IEC 61643-II Class-2 , Quality Standard ISO 9001, Environmental Standard ISO 14001, Luminaire shall have dual optics with primary optics distribution of 120 degree or higher and secondary optics as per site/boq requirement. All the luminaires shall have LM-79 , the testing facility to generate the LM-79 should be at vendor (Not Sub Vendor) address during production and LM-80 of LED shoulde be available. Radiation Emission Measurement as per CISPR.15:2018, Conducted Emission Measurement as per CISPR.15:2018, Output voltage ripple should be within 3%, Full Load Efficiency of the driver ≥ 85%. Luminaires and driver both shall be BIS certified individually. Heat sink used should be extruded Aluminum or Pressure Die-Cast Aluminum having high conductivity preferably ADC 12 or LM6. An extruded silicon loop gasket shall be provided in the lantern body to ensure a weather proof seal between the cover and the metal housing to exclude the entry of dust, water, insects, etc. Luminaire should conform to degree of protection of IP 65 or above. Mini IP68 water proof Gel box connector with PP Glue to be provided. Fixture should have beam distribution of 10° , 24° , 36°, 48° , 10X40° , 10X25° & 100X10° or as per consultant. Fixture should be compatible with accessory like honeycomb louvre as well as snoot for minimum glare. The product shall be complete with all factory-fitted accessories, mounting hardware, weatherproof cable entries and connectors required for proper installation including suitable foundation and operation. The manufacturers name/logo should be engraved/embossed on the housing/body or Name/Logo on aluminum plate labels or Name/logo printed on housing/body including jumper cable 5pin, 200W DC24V IP67 Driver, etc. complete as required and as approved by Engineer In Charge. Location: PILLAR | 60.00 | Each |  | 15000.00 | 900000.00 | 8900.00 | 534000.00 | 6466.00 | 387960.00 | 14838.00 | 890280.00 | 9000.00 | 540000.00 | 387960.00 | Instapower Ltd
3.00 | SITC of minimum 15W ( Lamp degree 36⁰ )surface mounted LED spot projector with delivered Luminous flux of minimum 35 lm/W. FIxture should have body in die-cast aluminium/extrusion and glass sealed optical chamber. The luminaire shall have a rated system lifetime of 50,000 burning hours at L70. The luminaire should have a colour temperature of RGBW and CRI > 70 and IK10 with IEC 60598 certification. The luminaire shall meet IP66 with THD < 10% and PF > 0.9. Operating Voltage 140-270VAC,The Surge Protection to be provided conforming to relevant IS standards/IEC 61643-II Class-2 , Quality Standard ISO 9001, Environmental Standard ISO 14001, Luminaire shall have dual optics with primary optics distribution of 120 degree or higher and secondary optics as per site/boq requirement. All the luminaires shall have LM-79 , the testing facility to generate the LM-79 should be at vendor (Not Sub Vendor) address during production and LM-80 of LED shoulde be available. Radiation Emission Measurement as per CISPR.15:2018, Conducted Emission Measurement as per CISPR.15:2018, Output voltage ripple should be within 3%, Full Load Efficiency of the driver ≥ 85%. Luminaires and driver both shall be BIS certified individually. Heat sink used should be extruded Aluminum or Pressure Die-Cast Aluminum having high conductivity preferably ADC 12 or LM6. An extruded silicon loop gasket shall be provided in the lantern body to ensure a weather proof seal between the cover and the metal housing to exclude the entry of dust, water, insects, etc. Luminaire should conform to degree of protection of IP 65 or above. Mini IP68 water proof Gel box connector with PP Glue to be provided. Fixture should have beam distribution of 10° , 24° , 36°, 48° , 10X40° , 10X25° & 100X10° or as per consultant. Fixture should be compatible with accessory like honeycomb louvre as well as snoot for minimum glare. The product shall be complete with all factory-fitted accessories, mounting hardware, weatherproof cable entries and connectors required for proper installation including suitable foundation and operation. The manufacturers name/logo should be engraved/embossed on the housing/body or Name/Logo on aluminum plate labels or Name/logo printed on housing/body including jumper cable 5pin, 200W DC24V IP67 Driver, etc. complete as required and as approved by Engineer In Charge. Location: TREES &PLANTERS | 300.00 | Each |  | 15000.00 | 4500000.00 | 8900.00 | 2670000.00 | 6466.00 | 1939800.00 | 14838.00 | 4451400.00 | 9000.00 | 2700000.00 | 1939800.00 | Instapower Ltd
4.00 | SITC of minimum 5Wm,3000K color, 24V flexible LED homogenous fixture for exterior top crown structure wash application. The housing of the material should be made of PCB Silicon Tube and the LEDs should be SMD type (SDCM <5). The delivered lumen output of the fixture should be around 40lm/W. The protection rating of the fixture should be IP67. Output power of the fixture should be 10-20W/M. The fixture should be of beam distribution of minimum 115˚. CCT of the fixture should be RGBW or as per requirement of the architect. The colour rendering capability of the fixture should be more the 80. The products shall be complete with all necessary accessories required for proper working of fixture including weather proof connection cables, water proof connectors,suitable LED drivers etc. Fixture should come with rigid Installation Aluminium profile for flex & Difusser as per site requirement etc. complete as required and as approved by Engineer In Charge. Location: CAB PICKUP AREA PLANTER EDGE | 500.00 | Mtr |  | 4000.00 | 2000000.00 | 5100.00 | 2550000.00 | 3725.00 | 1862500.00 | 4457.00 | 2228500.00 | 2800.00 | 1400000.00 | 1400000.00 | SYNERGY LIGHTING SOLUTIONS
5.00 | SITC of minimum 15W surface mounted LED Bollard fixture with delivered Luminous flux of minimum 60lm/W. FIxture should have body in die-cast aluminium/extrusion and glass sealed optical chamber. The luminaire shall have a rated system lifetime of 50,000 burning hours at L70. The luminaire should have a colour temperature of 3000k and CRI > 70 and IK10 with IEC 60598 certification. The luminaire shall meet IP66 with THD < 10% and PF > 0.9. Operating Voltage 140-240VAC,The Surge Protection to be provided conforming to relevant IS standards/IEC 61643-II Class-2 , Quality Standard ISO 9001, Environmental Standard ISO 14001, Luminaire shall have dual optics with primary optics distribution of 120degree or higher and secondary optics as per site/boq requirement. All the luminaires shall have LM-79 , the testing facility to generate the LM-79 should be at vendor (Not Sub Vendor) address during production and LM-80 of LED shoulde be available. Radiation Emission Measurement as per CISPR.15:2018, Conducted Emission Measurement as per CISPR.15:2018, Output voltage ripple should be within 3%, Full Load Efficiency of the driver ≥ 85%. The total power consumption should not exceed 20W (including driver). Luminaires and driver both shall be BIS certified individually. Heat sink used should be extruded Aluminum or Pressure Die-Cast Aluminum having high conductivity preferably ADC 12 or LM6. An extruded silicon loop gasket shall be provided in the lantern body to ensure a weather proof seal between the cover and the metal housing to exclude the entry of dust, water, insects, etc. Luminaire should conform to degree of protection of IP 65 or above. Mini 1P68 water proof Gel box connector with PP Glue to be provided. Fixture should have beam distribution of 60° , 120° , 180°, 360° , or as per consultant. The product shall be complete with all factory-fitted accessories, mounting hardware, weatherproof cable entries and connectors required for proper installation including suitable foundation and operation. Fixture dimension should be 750mmHeight and 150mm Dia as per fixture wattage. The manufacturers name/logo should be engraved/embossed on the housing/body or Name/Logo on aluminum plate labels or Name/logo printed on housing/body etc. complete as required and as approved by Engineer In Charge. Location: LANDSCAPE PATHWAY | 150.00 | Each |  | 8000.00 | 1200000.00 | 5500.00 | 825000.00 | 8065.00 | 1209750.00 | 5865.00 | 879750.00 | 9000.00 | 1350000.00 | 825000.00 | Awasthi Electric Works
6.00 | SITC of minimum 60W surface mounted LED POST TOP POLE LIGHT fixture with delivered Luminous flux of minimum 80lm/W. FIxture should have body in die-cast aluminium/extrusion and glass sealed optical chamber. The luminaire shall have a rated system lifetime of 50,000 burning hours at L70. The luminaire should have a colour temperature of 3000k and CRI > 70 and IK10 with IEC 60598 certification. The luminaire shall meet IP66 with THD < 10% and PF > 0.9. Operating Voltage 140-270VAC,The Surge Protection to be provided conforming to relevant IS standards/IEC 61643-II Class-2 , Quality Standard ISO 9001, Environmental Standard ISO 14001, Luminaire shall have dual optics with primary optics distribution of 120degree or higher and secondary optics as per site/boq requirement. All the luminaires shall have LM-79 , the testing facility to generate the LM-79 should be at vendor (Not Sub Vendor) address during production and LM-80 of LED shoulde be available. Radiation Emission Measurement as per CISPR.15:2018, Conducted Emission Measurement as per CISPR.15:2018, Output voltage ripple should be within 3%, Full Load Efficiency of the driver ≥ 85%. The total power consumption should not exceed 20W (including driver). Luminaires and driver both shall be BIS certified individually. Heat sink used should be extruded Aluminum or Pressure Die-Cast Aluminum having high conductivity preferably ADC 12 or LM6. An extruded silicon loop gasket shall be provided in the lantern body to ensure a weather proof seal between the cover and the metal housing to exclude the entry of dust, water, insects, etc. Luminaire should conform to degree of protection of IP 65 or above. Mini IP68 water proof Gel box connector with PP Glue to be provided. Fixture should have beam distribution of 60° , 120° , 180°, 360° , or as per consultant.The product shall be complete with all factory-fitted accessories, mounting hardware, weatherproof cable entries and connectors required for proper installation including suitable foundation and operation. Fixture dimension should be 2100mm Height / 2400mm Height as per fixture wattage. The manufacturers name/logo should be engraved/embossed on the housing/body or Name/Logo on aluminum plate labels or Name/logo printed on housing/body etc. complete as required and as approved by Engineer In Charge. Location: LANDSCAPE PATHWAY | 100.00 | Each |  | 8500.00 | 850000.00 | 27500.00 | 2750000.00 | 23510.00 | 2351000.00 | 8798.00 | 879800.00 | 39000.00 | 3900000.00 | 850000.00 | Balaji Engineering
7.00 | Supply of following sizes of 1.1 KV grade multicore copper conductor PVC insulated / XLPE insulated and PVC sheathed armoured cable as per IS-7098 (Part-I) 1988 respectively with upto date ammendments. 4C X 10 Sq mm | 4700.00 | Mtr |  | 715.00 | 3360500.00 | 870.00 | 4089000.00 | 1143.90 | 5376330.00 | 848.00 | 3985600.00 | 200.00 | 940000.00 | 940000.00 | SYNERGY LIGHTING SOLUTIONS
8.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in existing RCC/HUME/METAL/DWC HDPE pipe etc as required. Upto 35 sq. mm | 4300.00 | Mtr |  | 50.00 | 215000.00 | 20.00 | 86000.00 | 58.50 | 251550.00 | 12.00 | 51600.00 | 20.00 | 86000.00 | 51600.00 | epic enterprise
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in masonnary open duct etc as required. Upto 35 sq. mm | 200.00 | Mtr |  | 30.00 | 6000.00 | 20.00 | 4000.00 | 52.00 | 10400.00 | 12.00 | 2400.00 | 20.00 | 4000.00 | 2400.00 | epic enterprise
10.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Upto 35 sq. mm ( clamped with 1mm thick saddle) | 200.00 | Mtr |  | 30.00 | 6000.00 | 100.00 | 20000.00 | 58.50 | 11700.00 | 12.00 | 2400.00 | 25.00 | 5000.00 | 2400.00 | epic enterprise
11.00 | Supply of 50 mm dia HDPE pipe ISI marked conforming to IS 4984:2016 along with all accessories like socket, bend, couplers etc. complete as required. | 4300.00 | Mtr |  | 150.00 | 645000.00 | 160.00 | 688000.00 | 92.30 | 396890.00 | 37.00 | 159100.00 | 75.00 | 322500.00 | 159100.00 | epic enterprise
12.00 | Laying of 50 mm dia HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984:2016, complete with fitting and cutting, jointing etc. direct in ground including excavation and refilling the trench but excluding sand cushing and protectiove covering etc. complete as required. | 4300.00 | Mtr |  | 80.00 | 344000.00 | 110.00 | 473000.00 | 52.00 | 223600.00 | 37.00 | 159100.00 | 20.00 | 86000.00 | 86000.00 | SYNERGY LIGHTING SOLUTIONS
13.00 | Supplying and making end termination with brass compression gland and copper lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required. 4C X 10 Sq mm | 700.00 | Set |  | 350.00 | 245000.00 | 550.00 | 385000.00 | 680.00 | 476000.00 | 153.00 | 107100.00 | 50.00 | 35000.00 | 35000.00 | SYNERGY LIGHTING SOLUTIONS
14.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1 KV grade as required. 4C X 10 Sq mm | 20.00 | Set |  | 1000.00 | 20000.00 | 2000.00 | 40000.00 | 4164.00 | 83280.00 | 1224.00 | 24480.00 | 1000.00 | 20000.00 | 20000.00 | SYNERGY LIGHTING SOLUTIONS, Balaji Engineering
15.00 | Making horizontal boring of suitable dia. 50mm by using suitable mechanical arrangement, Sensor operated, Not lessthan 2.5Mtr Depth, horizontal bore well suitable for inserting of 50mm dia., HDPE Pipes. Job including supplying and laying of 50mm dia. PE-100 Grade, PN-8, HDPE Pipe in borewell hole including jointing, molding cutting, bending, etc. of pipes in boring hole as per site condition complete is required. | 100.00 | Mtr |  | 300.00 | 30000.00 | 1500.00 | 150000.00 | 1560.00 | 156000.00 | 404.00 | 40400.00 | 500.00 | 50000.00 | 30000.00 | Balaji Engineering
| Total in Figures |  |  |  |  | 17081500.00 |  | 17664000.00 |  | 15185860.00 |  | 14319410.00 |  | 12338500.00
Lowest Amount Quoted BY: SYNERGY LIGHTING SOLUTIONS(12338500.00)

## BOQ Summary
BOQ Summary Details Tender Title: Beautification of approach road to new terminal building with landscaping, hardscaping, horticulture and sculpture works and associated lighting works at Vijayawada International Airport. SH ELECTRICAL WORKS Tender ID: 2026_AAI_288828_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SYNERGY LIGHTING SOLUTIONS (BID ID -1065348) | 12338500.00 | L1
| 2 | epic enterprise (BID ID -1065354) | 14319410.00 | L2
| 3 | Instapower Ltd (BID ID -1066595) | 15185860.00 | L3
| 4 | Balaji Engineering (BID ID -1065447) | 17081500.00 | L4
| 5 | Awasthi Electric Works (BID ID -1065539) | 17664000.00 | L5