## BoQ1
Government eProcurement System Created By: SINDHU L S Created Date/Time: 22-Oct-2026 04:41 PM Tender Title: Replacement of existing Light Fittings in Intake Substation, Old Fire Station, New Fire Station, Admin Power House and Cargo power House along with associated cabling works at Chennai Airport Tender ID: 2026_AAI_291206_1
Tender Inviting Authority: AGM (E-E), Chennai Airport, Chennai.
Name of Work: Replacement of existing Light Fittings in Intake Substation, Old Fire Station, New Fire Station, Admin Power House and Cargo power House along with associated cabling works at Chennai Airport.
E BID No : 2026_AAI_291206_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | C P MONCHESTER ELECTRICALS (GSTN-33AJOPP7842E1ZY) BID ID -1076693 |  | CHENNAI ENGINEERING SERVICES (GSTN-33AADFC4373K1ZH) BID ID -1081570 |  | DElite System Engineering (India) Pvt. Ltd. (GSTN-NA) BID ID -1078838 |  | METRO LIGHTS (GSTN-NA) BID ID -1078855 |  | Udaya Technologies Private Limited (GSTN-NA) BID ID -1081607
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of LED Highbay Luminaire having minimum lumen output of 24000 lumens made of Powder coated Pressure die cast Aluminium body of thickness ≥ 1.5 mm and having Minimum Lumen Efficacy 160 lm/W, Inbuilt Driver, Input voltage range 140-270 Volt AC, 50Hz, Internal surge protection > 4 KV, Driver efficiency > 85%,THD < 10%, PF ≥ 0.95, IP 66, IK ≥ 08, CRI ≥ 70, Minimum 50000 Burning Hours, CCT 5700K (As per ANSI Bin), 5 year warranty from OEM, Maximum power consumption should not be more than 110% of the specified rating etc., complete as required and meeting the Techno Commericial Specifications (TCS). | 45.00 | Each |  | 7200.00 | 324000.00 | 5499.00 | 247455.00 | 6599.00 | 296955.00 | 3955.00 | 177975.00 | 6624.00 | 298080.00 | 177975.00 | METRO LIGHTS
2.00 | Supply of following capacity LED Flood Light Luminaire having minimum lumen output as below, made of Powder coated Pressure die cast Aluminium body of thickness ≥ 1.5 mm and having Minimum Lumen Efficacy 120 lm/W, Inbuilt Driver, Input voltage range 140 - 270 Volt AC, 50 Hz, Internal surge protection > 4 KV, Driver efficiency > 85%, THD < 10%, PF ≥ 0.95, IP 66, IK ≥ 08, CRI ≥ 70, Minimum 50000 Burning Hours, CCT 5700K (As per ANSI Bin), 5 year warranty from OEM, Maximum power consumption should not be more than 110% of the specified rating etc., complete as required and meeting the Techno Commericial Specifications (TCS).
2.01 | Minimum lumen output of 9600 lumens | 145.00 | Each |  | 2910.00 | 421950.00 | 2999.00 | 434855.00 | 3299.00 | 478355.00 | 1921.00 | 278545.00 | 5316.00 | 770820.00 | 278545.00 | METRO LIGHTS
2.02 | Minimum lumen output of 18000 lumens | 10.00 | Each |  | 7200.00 | 72000.00 | 4999.00 | 49990.00 | 5599.00 | 55990.00 | 3955.00 | 39550.00 | 3489.28 | 34892.80 | 34892.80 | Udaya Technologies Private Limited
3.00 | Supply of LED Well Glass Light Fixture having minimum lumen output of 4000 lumens, made of Powder coated Pressure die cast Aluminium body of thickness ≥ 1.5 mm with Polycarbonate milky shade diffuser and having Minimum Lumen Efficacy 100 lm/W, , Inbuilt Driver, Input voltage range 140 - 270 Volt AC, 50Hz, Internal surge protection > 4 KV, Driver efficiency > 85%, THD < 10%, PF ≥ 0.95, IP66, CRI ≥ 80, Minimum 50000 Burning Hours, CCT 5700K (As per ANSI Bin), 5 year warranty from OEM, Maximum power consumption should not be more than 110% of the specified rating etc., complete as required and meeting the Techno Commericial Specifications (TCS). | 270.00 | Each |  | 1410.00 | 380700.00 | 1299.00 | 350730.00 | 1499.00 | 404730.00 | 712.00 | 192240.00 | 1397.00 | 377190.00 | 192240.00 | METRO LIGHTS
4.00 | Supply of 2 ft x 2 ft Recess mounted LED fixture having minimum lumen output of 4300 lumens, made of Aluminium body of thickness ≥ 0.5mm and having Minimum Lumen Efficacy 120 lm/W, Inbuilt Driver, Input voltage Range 140-270 Volt AC, 50Hz, Internal surge protection of >4 KV, Driver efficiency > 85%, THD < 10% , PF ≥ 0.95, IP20, CRI ≥ 80, Minimum 50000 Burning Hours, CCT 6500K (As per ANSI Bin), Maximum power consumption should not be more than 110% of the specified rating, 5 year warranty from OEM etc.. complete as required and meeting the Techno Commericial Specifications (TCS). | 148.00 | Each |  | 1200.00 | 177600.00 | 1799.00 | 266252.00 | 1899.00 | 281052.00 | 961.00 | 142228.00 | 2521.00 | 373108.00 | 142228.00 | METRO LIGHTS
5.00 | Supply of LED surface mounted Batten light having minimum lumen output of 4800 lumens made of aluminium body (Thickness ≥ 1.0 mm ) and having minimum Lumen Efficacy 120 lm/W, Input voltage Range 140-270 Volt AC, 50Hz, Internal surge protection of >4 KV, Driver efficiency > 85%, THD < 10% , PF ≥ 0.95, IP20, CRI ≥ 80, life time of minimum 50000 Burning Hours with, CCT 6500K (As per ANSI Bin), SDCM(Standard Deviation Color Matching) <5, Maximum power consumption should not be more than 110% of the specified rating, 5 year warranty from OEM etc. complete as required and meeting the Techno Commercial Specifications (TCS). | 150.00 | Each |  | 360.00 | 54000.00 | 2449.00 | 367350.00 | 1199.00 | 179850.00 | 610.00 | 91500.00 | 1294.00 | 194100.00 | 54000.00 | C P MONCHESTER ELECTRICALS
6.00 | Supply of LED street light fitting having minimum lumen output of 14400 lumens, system efficacy of not less than 120 lumens per watt, beam angle 60-120 degree, Inbuilt Driver, Input voltage range 140-270 Volt AC, 50Hz, Internal surge protection > 4 KV, Driver efficiency > 85%,THD < 10%, PF ≥ 0.95, IP 66, IK ≥ 08, CRI ≥ 70, Minimum 50000 Burning Hours, CCT 6500K (As per ANSI Bin), 5 year warranty from OEM, Maximum power consumption should not be more than 110% of the specified rating etc., complete as required and meeting the Techno Commericial Specifications (TCS). | 10.00 | Each |  | 4500.00 | 45000.00 | 5999.00 | 59990.00 | 4299.00 | 42990.00 | 2825.00 | 28250.00 | 3577.00 | 35770.00 | 28250.00 | METRO LIGHTS
7.00 | Installation, Testing and Commissioning of ceiling / surface mounted LED Highbay/ Flood light fittings of all sizes and shapes on ceiling height upto 7 meters, including Supply & Fixing suitable size heavyduty clamp/anchor fastener hook as required as per site requirement with all accessories including connections with 2.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc., complete as required (All the wires visible outside should be covered with suitable sleeve for aesthetics). | 200.00 | Each |  | 300.00 | 60000.00 | 299.00 | 59800.00 | 199.00 | 39800.00 | 339.00 | 67800.00 | 394.00 | 78800.00 | 39800.00 | DElite System Engineering (India) Pvt. Ltd.
8.00 | Installation, testing and commissioning of LED Well Glass Light Fixture complete with all accessories etc. Suspended from Ceiling with 20 mm dia X 1.6 mm thick MS pipe class B of length 6 feet including connections with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing, with suitable size clamp, hook & supports etc. complete as required. | 270.00 | Each |  | 360.00 | 97200.00 | 699.00 | 188730.00 | 399.00 | 107730.00 | 565.00 | 152550.00 | 630.00 | 170100.00 | 97200.00 | C P MONCHESTER ELECTRICALS
9.00 | Installation, testing and commissioning of Recess mounted 2 x 2 ft LED Light fittings with all accessories including connections with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing, SS chain protection etc. complete as required. | 148.00 | Each |  | 165.00 | 24420.00 | 399.00 | 59052.00 | 99.00 | 14652.00 | 339.00 | 50172.00 | 286.00 | 42328.00 | 14652.00 | DElite System Engineering (India) Pvt. Ltd.
10.00 | Installation, testing and commissioning of surface mounted 4 ft LED Batten Light fittings with all accessories including installation of fixture, connections with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. complete as required. | 150.00 | Each |  | 93.00 | 13950.00 | 199.00 | 29850.00 | 99.00 | 14850.00 | 170.00 | 25500.00 | 190.00 | 28500.00 | 13950.00 | C P MONCHESTER ELECTRICALS
11.00 | Installation, testing and commissioning of LED street light fitting with all accessories on existing street light pole of 7 mtr height with bracket, including supplying and drawing of PVC sheathed 3 core 1.5 sq.mm. multicore flexible copper wire from loop-in-loop-out box upto the individual streetlight fitting(s), terminations of wire, including earthing connections etc. complete as required & as specified. | 10.00 | job |  | 450.00 | 4500.00 | 3999.00 | 39990.00 | 999.00 | 9990.00 | 509.00 | 5090.00 | 190.00 | 1900.00 | 1900.00 | Udaya Technologies Private Limited
12.00 | Dismantling of all types old light fixtures installed on ceiling/suspended & shifting the same to AAI store etc., complete as required. | 546.00 | Each |  | 36.00 | 19656.00 | 99.00 | 54054.00 | 99.00 | 54054.00 | 113.00 | 61698.00 | 143.00 | 78078.00 | 19656.00 | C P MONCHESTER ELECTRICALS
13.00 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
13.01 | 20mm | 500.00 | Mtr |  | 120.00 | 60000.00 | 229.00 | 114500.00 | 399.00 | 199500.00 | 124.00 | 62000.00 | 185.00 | 92500.00 | 60000.00 | C P MONCHESTER ELECTRICALS
13.02 | 25mm | 100.00 | Mtr |  | 140.00 | 14000.00 | 249.00 | 24900.00 | 399.00 | 39900.00 | 158.00 | 15800.00 | 182.00 | 18200.00 | 14000.00 | C P MONCHESTER ELECTRICALS
14.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required. 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 250.00 | Mtr |  | 210.00 | 52500.00 | 349.00 | 87250.00 | 399.00 | 99750.00 | 198.00 | 49500.00 | 629.00 | 157250.00 | 49500.00 | METRO LIGHTS
15.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point ( without independent switch etc.) with 2.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed PVC conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 50.00 | Point |  | 1200.00 | 60000.00 | 899.00 | 44950.00 | 1100.00 | 55000.00 | 396.00 | 19800.00 | 1240.00 | 62000.00 | 19800.00 | METRO LIGHTS
16.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
16.01 | 3 x 1.5 sq. mm | 500.00 | Mtr |  | 120.00 | 60000.00 | 109.00 | 54500.00 | 299.00 | 149500.00 | 89.00 | 44500.00 | 113.00 | 56500.00 | 44500.00 | METRO LIGHTS
16.02 | 6 x 1.5 sq. mm | 100.00 | Mtr |  | 210.00 | 21000.00 | 199.00 | 19900.00 | 799.00 | 79900.00 | 164.00 | 16400.00 | 197.00 | 19700.00 | 16400.00 | METRO LIGHTS
17.00 | Supply of Aluminium Conductor, XLPE insulated, PVC sheathed, armoured power cable of 1.1 KV grade of following sizes conforming to IS 7098 (Part-1) as amended upto date as required.
17.01 | 3C x 4 Sqmm | 150.00 | Mtr |  | 240.00 | 36000.00 | 159.00 | 23850.00 | 209.00 | 31350.00 | 88.00 | 13200.00 | 129.00 | 19350.00 | 13200.00 | METRO LIGHTS
17.02 | 4C x 6 sq.mm. | 300.00 | Mtr |  | 270.00 | 81000.00 | 219.00 | 65700.00 | 209.00 | 62700.00 | 119.00 | 35700.00 | 129.00 | 38700.00 | 35700.00 | METRO LIGHTS
18.00 | Supply of Aluminium Conductor, XLPE insulated, PVC sheathed, armoured power cable of 1.1 KV grade of following sizes conforming to IS 7098 (Part-1) as amended upto date as required. 4core 16 sqmm | 120.00 | Mtr |  | 360.00 | 43200.00 | 219.00 | 26280.00 | 299.00 | 35880.00 | 172.00 | 20640.00 | 177.00 | 21240.00 | 20640.00 | METRO LIGHTS
19.00 | Supply of PE80 PN6 32mm dia HDPE pipe conforming to IS 4984 as amended upto dated etc as required | 120.00 | Mtr |  | 180.00 | 21600.00 | 49.00 | 5880.00 | 399.00 | 47880.00 | 62.00 | 7440.00 | 57.00 | 6840.00 | 5880.00 | CHENNAI ENGINEERING SERVICES
20.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing HDPE pipe as required. Upto 35sqmm | 120.00 | Mtr |  | 45.00 | 5400.00 | 39.00 | 4680.00 | 49.00 | 5880.00 | 136.00 | 16320.00 | 82.00 | 9840.00 | 4680.00 | CHENNAI ENGINEERING SERVICES
21.00 | Laying and fixing of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of following size on wall surface as required. Upto 35 sq.mm (clamped with 1mm MS flat clamp) | 450.00 | Mtr |  | 90.00 | 40500.00 | 99.00 | 44550.00 | 109.00 | 49050.00 | 136.00 | 61200.00 | 82.00 | 36900.00 | 36900.00 | Udaya Technologies Private Limited
22.00 | Laying of one number HDPE of following size direct in ground including excavation and refilling the trench etc as required 32mm dia | 120.00 | Mtr |  | 210.00 | 25200.00 | 69.00 | 8280.00 | 399.00 | 47880.00 | 57.00 | 6840.00 | 245.00 | 29400.00 | 6840.00 | METRO LIGHTS
23.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 240.00 | Mtr |  | 33.00 | 7920.00 | 39.00 | 9360.00 | 79.00 | 18960.00 | 28.00 | 6720.00 | 57.00 | 13680.00 | 6720.00 | METRO LIGHTS
24.00 | Supply and fixing of hinged door Weather proof IP66 junction Box (similar to Hensel: KF1000G) on the wall surface including Providing & Fixing suitable connectors/terminals for loop in & loop out cables of 3 core 4 sqmm. armoured aluminium cable, 6/10 Amp SPN MCB, DIN bar of suitable size, 1 No. IP66 cable gland (for outgoing for LED Light fixture) etc., complete as required. | 20.00 | Each |  | 3000.00 | 60000.00 | 2199.00 | 43980.00 | 1999.00 | 39980.00 | 1130.00 | 22600.00 | 4398.00 | 87960.00 | 22600.00 | METRO LIGHTS
25.00 | Supplying and making end termination with IP66 weather proof fully insulated brass PBT cable gland (Similar to Hensel: GSC21) and Aluminium lugs of suitable size for 4C x 6 sqmm/3C x 4 sqmm size of PVC insulated and PVC sheathed/XLPE Aluminium conductor cable of 1.1 KV grade etc., complete as required. | 40.00 | Set |  | 2100.00 | 84000.00 | 1299.00 | 51960.00 | 1199.00 | 47960.00 | 791.00 | 31640.00 | 926.00 | 37040.00 | 31640.00 | METRO LIGHTS
26.00 | Supply of 7 mtrs. high GI OCTAGONAL continuously tapered galvanised street light pole with Single arm GI Bracket upto 1.5m long, diameter suitable for installation of LED street light luminaire, designed for wind velocity as per IS 875 (but not less than 50 m/sec.), fabricated out of 3 mm MS plate in single section, suitable for installation on a precast foundation with supply of 4 Nos. of foundation bolt & anchor plate, rigid flange plate (200x200x12mm min.) welded with the base of pole for fixing on foundation bolts complete as reqd. for structural stability as specified, weather proof and vandal resistant door flush with the exterior surface containing a terminal plate of 5 mm thick backlite sheet with 32 Amp heavy duty connector for loop in loop out cable terminations suitable for upto two numbers 4 core 25 Sq.mm cables & 6A DP MCB for each fixture connections, earthing bolts for continuous earth connection complete as required & as specified. | 10.00 | Each |  | 12000.00 | 120000.00 | 9999.00 | 99990.00 | 15500.00 | 155000.00 | 13560.00 | 135600.00 | 14107.00 | 141070.00 | 99990.00 | CHENNAI ENGINEERING SERVICES
27.00 | Erection of 7 Mtr.high G.I.OCTAGONAL street light pole & bracket with all accessories in reinforced cement concrete 1:2:4 (1 cement : 2 coarse sand : 4graded stone aggregate 40 mm nominal size) foundation including excavation and refilling including positioning of template & foundation bolts (supplied with pole to match with pole base plate) & providing and fixing of PE63 PN6 HDPE pipe of size 50 mm dia (2 pieces of min. 0.75 m length) in the foundation for loop-in-loop-out of the cable to the pole complete as required and as specified. The depth of concrete foundation shall be as per the design of pole OEM, Length and width shall be more than dimension of base plate. | 10.00 | Job |  | 5600.00 | 56000.00 | 7999.00 | 79990.00 | 12000.00 | 120000.00 | 8475.00 | 84750.00 | 13630.00 | 136300.00 | 56000.00 | C P MONCHESTER ELECTRICALS
| Total in Figures |  |  |  |  | 2543296.00 |  | 3018598.00 |  | 3267068.00 |  | 1963748.00 |  | 3468136.80
Lowest Amount Quoted BY: METRO LIGHTS(1963748.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of existing Light Fittings in Intake Substation, Old Fire Station, New Fire Station, Admin Power House and Cargo power House along with associated cabling works at Chennai Airport Tender ID: 2026_AAI_291206_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | METRO LIGHTS (BID ID -1078855) | 1963748.00 | L1
| 2 | C P MONCHESTER ELECTRICALS (BID ID -1076693) | 2543296.00 | L2
| 3 | CHENNAI ENGINEERING SERVICES (BID ID -1081570) | 3018598.00 | L3
| 4 | DElite System Engineering (India) Pvt. Ltd. (BID ID -1078838) | 3267068.00 | L4
| 5 | Udaya Technologies Private Limited (BID ID -1081607) | 3468136.80 | L5