## BoQ1
Government eProcurement System Created By: YOGESH KUMAR Created Date/Time: 04-Aug-2026 04:56 PM Tender Title: Replacement of the Pumps and Pipelines in Pump House from underground sump to overhead tank at EFA Tender ID: 2026_AVNL_280845_1
Tender Inviting Authority: The Chief General Manager, Engine Factory Avadi (A Unit of AVNL)
Name of Work: Replacement of the Pumps and Pipelines in Pump House from underground sump to overhead tank at EFA
Contract No: EFA/EO(C)/1281/E/TE/06/2026-27
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | HARI ENTERPRISES (GSTN-NA) BID ID -1038791 |  | N.F.LEL CONSTRUCTION (GSTN-NA) BID ID -1041829 |  | SADH BUILDERS (GSTN-NA) BID ID -1038845 |  | S VINAYAGAMURTHY (GSTN-NA) BID ID -1038846
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply and Installation and Comissioning of Horizontal Centrifugal Pump ( Split Case) Model : UP 100/38 of make Kirloskar Pump or equivalant model from C.R.I. Pumps / Texmo Pump/Grundfos with Flow Rate: min 150 m3/hr and Head: 45m combined with motor of 37 KW, 1450 RPM IE3 , Suction Pipe Dia : 150 and Delivery Pipe Dia : 100mm , including Erection of pump set with appropiate foundation as per details given in datasheet of Pump manufacturer. | 1.00 | EACH | 359144.80 | 360000.00 | 360000.00 | 500000.00 | 500000.00 | 749000.00 | 749000.00 | 410000.00 | 410000.00 | 360000.00 | HARI ENTERPRISES
2.00 | Supply and Installation and Comissioning of Vertical Multistage Pump Model : BHR 28-18 of make Kirloskar Pump or equivalant model from C.R.I. Pumps / Texmo Pump/Grundfos with Flow Rate: min 140 m3/hr and Head: 50m combined with motor of 37 KW, 1450 RPM IE3, Suction and Delivery Pipe Dia : 200mm, including Erection of pump set with appropiate foundation as per details given in datasheet of Pump manufacturer. | 1.00 | EACH | 1298969.96 | 1300000.00 | 1300000.00 | 1250000.00 | 1250000.00 | 670000.00 | 670000.00 | 1350000.00 | 1350000.00 | 670000.00 | SADH BUILDERS
3.00 | Supply and Installation of Starter for 2 No.s of pump of 37KW/ 50hp panel ( 1000 * 1200 * 300) which consist of incomer 250 A TPN MCCB, Rotary Handle, Spreader link, sub incomer 125 tpn MCCB, 50A contactor, OLR 30-50 A, SPP, including necessary cable and accessories. | 2.00 | EACH | 180470.38 | 180000.00 | 360000.00 | 250000.00 | 500000.00 | 198000.00 | 396000.00 | 180000.00 | 360000.00 | 360000.00 | HARI ENTERPRISES, S VINAYAGAMURTHY
4.00 | Supply And Fixing Of Stainless Steel 304 Grade Schedule 10 Pipe of 150mm Dia | 108.00 | RM | 15650.34 | 14600.00 | 1576800.00 | 7500.00 | 810000.00 | 9000.00 | 972000.00 | 13300.00 | 1436400.00 | 810000.00 | N.F.LEL CONSTRUCTION
5.00 | Supply And Fixing Of Stainless Steel 304 Grade Schedule 10 Pipe of 100mm Dia | 4.00 | RM | 7605.10 | 7500.00 | 30000.00 | 6300.00 | 25200.00 | 4990.00 | 19960.00 | 7200.00 | 28800.00 | 19960.00 | SADH BUILDERS
6.00 | Supply And Fixing 150x100 mm Stainless Steel Reducer Schedule 10 | 1.00 | NOS | 3894.00 | 2600.00 | 2600.00 | 6500.00 | 6500.00 | 3800.00 | 3800.00 | 3895.00 | 3895.00 | 2600.00 | HARI ENTERPRISES
7.00 | Supply And Fixing 200x150 Mm Stainless Steel Reducer Schedule 10 | 1.00 | NOS | 4838.00 | 4400.00 | 4400.00 | 7500.00 | 7500.00 | 3900.00 | 3900.00 | 4835.00 | 4835.00 | 3900.00 | SADH BUILDERS
8.00 | Supply And Fixing Stainless Steel 304 Grade 150mm Dia Flanges Class 150 of 18mm Thickness With Gasket | 28.00 | NOS | 4148.88 | 4100.00 | 114800.00 | 7500.00 | 210000.00 | 4900.00 | 137200.00 | 4148.00 | 116144.00 | 114800.00 | HARI ENTERPRISES
9.00 | Supply And Fixing Stainless Steel 304 Grade 100mm Dia Flanges Class 150 of 18mm Thickness With Gasket | 2.00 | NOS | 3004.75 | 3000.00 | 6000.00 | 7000.00 | 14000.00 | 3900.00 | 7800.00 | 3000.00 | 6000.00 | 6000.00 | HARI ENTERPRISES, S VINAYAGAMURTHY
10.00 | Supply And Fixing Stainless Steel Bolt ,Nuts And Washer Set M18 X 65 Mm | 220.00 | NOS | 608.88 | 600.00 | 132000.00 | 200.00 | 44000.00 | 149.00 | 32780.00 | 605.00 | 133100.00 | 32780.00 | SADH BUILDERS
11.00 | Supply And Fixing Stainless Steel Bolt ,Nuts And Washer Set M18 X 120 Mm | 8.00 | NOS | 858.09 | 800.00 | 6400.00 | 300.00 | 2400.00 | 249.00 | 1992.00 | 858.00 | 6864.00 | 1992.00 | SADH BUILDERS
12.00 | Supply And Fixing Stainless Steel U Bolts 300mm For Pipe Clamping | 12.00 | NO.S | 509.76 | 500.00 | 6000.00 | 400.00 | 4800.00 | 499.00 | 5988.00 | 509.00 | 6108.00 | 4800.00 | N.F.LEL CONSTRUCTION
13.00 | Supply And Fixing 15mm Stainless Steel Nipple For Pressure Gauge | 4.00 | NO.S | 261.96 | 250.00 | 1000.00 | 250.00 | 1000.00 | 499.00 | 1996.00 | 261.00 | 1044.00 | 1000.00 | HARI ENTERPRISES, N.F.LEL CONSTRUCTION
14.00 | Supply And Fixing Of Stainless Steel 304 Grade 150mm Dia Bend | 8.00 | NO.S | 8555.00 | 6500.00 | 52000.00 | 9500.00 | 76000.00 | 3990.00 | 31920.00 | 8555.00 | 68440.00 | 31920.00 | SADH BUILDERS
15.00 | Supply And Fixing Of Stainless Steel 304 Grade 150mm Dia Tee | 1.00 | NO.S | 11564.00 | 7000.00 | 7000.00 | 12000.00 | 12000.00 | 5990.00 | 5990.00 | 11564.00 | 11564.00 | 5990.00 | SADH BUILDERS
16.00 | Supply Of 150mm Dia Cast Steel Gate Valve ( Make: Kirloskar) Of Class 150 With SS 304 Spindle | 4.00 | NO.S | 54940.80 | 55000.00 | 220000.00 | 60000.00 | 240000.00 | 44900.00 | 179600.00 | 49000.00 | 196000.00 | 179600.00 | SADH BUILDERS
17.00 | Labour For Fixing of 150mm Dia Cast Steel Gate Valve ( Make: Kirloskar) Of Class 150 With SS 304 Spindle | 2.00 | NO.S | 7080.00 | 6500.00 | 13000.00 | 75000.00 | 150000.00 | 2990.00 | 5980.00 | 7080.00 | 14160.00 | 5980.00 | SADH BUILDERS
18.00 | Supply of 150mm Dia Cast Steel CHECK Valve ( Make: Kirloskar) With SS 304 Spindle | 4.00 | NO.S | 57985.20 | 58000.00 | 232000.00 | 75000.00 | 300000.00 | 36900.00 | 147600.00 | 54000.00 | 216000.00 | 147600.00 | SADH BUILDERS
19.00 | Labour For Fixing Of 150mm Dia Cast Steel CHECK Valve ( Make: Kirloskar) With SS 304 Spindle | 2.00 | NO.S | 7039.88 | 7000.00 | 14000.00 | 8500.00 | 17000.00 | 3900.00 | 7800.00 | 7020.00 | 14040.00 | 7800.00 | SADH BUILDERS
20.00 | Supply of 150mm Dia CI Foot Valve Ball Type K519 ( Make: Kartar) | 2.00 | NO | 18273.48 | 17000.00 | 34000.00 | 25000.00 | 50000.00 | 19500.00 | 39000.00 | 15650.00 | 31300.00 | 31300.00 | S VINAYAGAMURTHY
21.00 | Labour For Fixing Of 150mm Dia CI Foot Valve Ball Type K519 ( Make: Kartar) | 1.00 | NO | 7080.00 | 7000.00 | 7000.00 | 5000.00 | 5000.00 | 2950.00 | 2950.00 | 7080.00 | 7080.00 | 2950.00 | SADH BUILDERS
22.00 | Supply of Pressure Gauge With Range 0 To 25 Bar Of 4" Size ( 100mm) Ns 63 ( Make: Wika) | 4.00 | NO.S | 6244.56 | 4000.00 | 16000.00 | 26000.00 | 104000.00 | 3980.00 | 15920.00 | 5950.00 | 23800.00 | 15920.00 | SADH BUILDERS
23.00 | Labour For Fixing of Pressure Gauge With Range 0 To 25 Bar Of 4" Size ( 100mm) Ns 63 ( Make: Wika) | 2.00 | NO.S | 1000.00 | 1000.00 | 2000.00 | 5000.00 | 10000.00 | 999.00 | 1998.00 | 1000.00 | 2000.00 | 1998.00 | SADH BUILDERS
24.00 | Supply of Pressure Switch For 0 to 25 Bar Pressure Gauge ( Make: Wika) | 4.00 | NO.S | 5664.00 | 4000.00 | 16000.00 | 55000.00 | 220000.00 | 7899.00 | 31596.00 | 5660.00 | 22640.00 | 16000.00 | HARI ENTERPRISES
25.00 | Labour For Fixing Of Pressure Switch For 0 To 25 Bar Pressure Gauge ( Make: Wika) | 2.00 | NO.S | 2500.00 | 1197.00 | 2394.00 | 5000.00 | 10000.00 | 1000.00 | 2000.00 | 2500.00 | 5000.00 | 2000.00 | SADH BUILDERS
26.00 | Supply And Fixing Of 150mm Dia Cast Iron Buterfly Valve ( Make: Kirloskar) | 1.00 | NO | 10237.68 | 10000.00 | 10000.00 | 12000.00 | 12000.00 | 9800.00 | 9800.00 | 10230.00 | 10230.00 | 9800.00 | SADH BUILDERS
27.00 | Labour including tools, tackles, equipments for site clearance such as cutting of bushes removing of plants including uprooting of roots of plants and levelling the ground and clearing the site for working as specified and directed by the Engineer-In-Charge. | 50.15 | SQM | 20.59 | 25.00 | 1253.75 | 25.00 | 1253.75 | 100.00 | 5015.00 | 20.00 | 1003.00 | 1003.00 | S VINAYAGAMURTHY
28.00 | Surface excavation n.exc (not exceeding) 30 cm deep and averaging 15cm deep and getting out in hard and dense soil | 50.15 | SQM | 107.18 | 100.00 | 5015.00 | 150.00 | 7522.50 | 150.00 | 7522.50 | 95.00 | 4764.25 | 4764.25 | S VINAYAGAMURTHY
29.00 | Dismantling of mild steel work of any description including steel window , guard bars and shed | 3.90 | Quintal | 661.13 | 750.00 | 2925.00 | 3000.00 | 11700.00 | 1000.00 | 3900.00 | 575.00 | 2242.50 | 2242.50 | S VINAYAGAMURTHY
30.00 | Demolition of Cement Concrete(Reinforced) in Sunshade and RCC Platform & cable trenches Complete all as specified and as directed by the Engineer-in-Charge. | 1.24 | CUM | 2166.26 | 2000.00 | 2480.00 | 4000.00 | 4960.00 | 500.00 | 620.00 | 1880.00 | 2331.20 | 620.00 | SADH BUILDERS
31.00 | M/L Excavation in trenches, n. exc. 1.5m wide and n.exc. 1.5m in depth for foundation etc. And getting out including dressing/ trimming sides and levelling/ grading and ramming of bottoms of excavation in hard and dense soil. | 21.60 | CU.M | 776.25 | 600.00 | 12960.00 | 350.00 | 7560.00 | 600.00 | 12960.00 | 750.00 | 16200.00 | 7560.00 | N.F.LEL CONSTRUCTION
32.00 | Returning, filling in, including spreading, levelling, watering and well ramming in layers not exc 25 cm. in hard and dense soil. | 19.40 | CU.M | 159.97 | 100.00 | 1940.00 | 300.00 | 5820.00 | 200.00 | 3880.00 | 145.00 | 2813.00 | 1940.00 | HARI ENTERPRISES
33.00 | Material and Labour for Sand filling under floors or in foundations including watering and consolidation work as directed by the E-In-Charge. | 4.14 | CUM | 2270.45 | 2600.00 | 10764.00 | 3000.00 | 12420.00 | 700.00 | 2898.00 | 1975.00 | 8176.50 | 2898.00 | SADH BUILDERS
34.00 | M&L for providing plain cement concrete 1:4:8 type D2 using 40mm graded aggregate in Ditto in walls or retaining walls, any thickness, size or shape including pilasters, buttresses columns, pillars, boundary pillars and posts (including caps and bases) complete as directed by the Engineer-In-Charge. | 5.52 | CUM | 7146.56 | 5800.00 | 32016.00 | 8000.00 | 44160.00 | 7000.00 | 38640.00 | 6215.00 | 34306.80 | 32016.00 | HARI ENTERPRISES
35.00 | M& L of Cement concrete type B-1, 1:2:4 (20mm graded aggregate) for hardstanding floor 85mm thickness (180.2+4*90.6) | 55.25 | SQ.M. | 623.99 | 650.00 | 35912.50 | 1500.00 | 82875.00 | 7400.00 | 408850.00 | 540.00 | 29835.00 | 29835.00 | S VINAYAGAMURTHY
36.00 | M&L for providing reinforcement cement concrete 1:1.5:3 M 20 using 20 mm graded aggregate in Foundations, including rafts, footings, foundation beams; plinth beams; bases for columns, etc.; basement slabs, under- reamed piles and mass concrete as directed by the E-In-Charge | .50 | CUM | 8498.41 | 9000.00 | 4500.00 | 11000.00 | 5500.00 | 8000.00 | 4000.00 | 6500.00 | 3250.00 | 3250.00 | S VINAYAGAMURTHY
37.00 | S&F of TMT MS bars 6mm to 8mm dia, cut to length,bend to shape required, including cranking,bending spirally for hooping for columns,hooking ends and binding with and including mild steel wire(annealed) not less than 0.9mm dia.or securing with clips as directed by the Engineer-In-Charge. | 32.00 | KG | 97.23 | 125.00 | 4000.00 | 100.00 | 3200.00 | 130.00 | 4160.00 | 95.00 | 3040.00 | 3040.00 | S VINAYAGAMURTHY
38.00 | S/F for gates of angle or other section with gusset plates, rails, braces, etc., complete, drilled for fixing of steel sheeting or other covering. Doors, etc. to be prepared for hanging or sliding with and including either hooks and hinges or steel hanging door fittings (exclusive of steel sheeting or other covering, running rails and guides) and hanging; also fastening and fixing complete, Fe 410-W (Gde-E- 250)quality-A with heavy heavy duty ball bearing hinges, | 250.00 | KGS. | 137.03 | 165.00 | 41250.00 | 220.00 | 55000.00 | 150.00 | 37500.00 | 130.00 | 32500.00 | 32500.00 | S VINAYAGAMURTHY
39.00 | M&L for brickwork with subclass B bricks, in straight or curved on plan exc 6m mean radius, built in CM 1:4 complete all as specified and as directed by the Engineer-in-Charge | 1.40 | CUM | 6405.50 | 7000.00 | 9800.00 | 9500.00 | 13300.00 | 8000.00 | 11200.00 | 6000.00 | 8400.00 | 8400.00 | S VINAYAGAMURTHY
40.00 | M& L Rendering 15mm thick cement plaster n fair faces of brickwork or concrete sur- face using cement morter (1:4) on Inner wall (204.80+58.32) | 8.50 | SQ.M | 302.59 | 400.00 | 3400.00 | 425.00 | 3612.50 | 400.00 | 3400.00 | 280.00 | 2380.00 | 2380.00 | S VINAYAGAMURTHY
41.00 | Removing of material like debris up to a distance at 1.0 km including , lead , lift transportation etc. as directed by the E-in- charge .(one load represents one tone ) beyond the lead included in the rates, including loading, unloading and stacking at the destination Complete all as specified and as directed by the E-in -charge. | 5.25 | LOAD | 269.10 | 288.00 | 1512.00 | 3000.00 | 15750.00 | 700.00 | 3675.00 | 1000.00 | 5250.00 | 1512.00 | HARI ENTERPRISES
42.00 | Providing and fixing double scaffolding system (cup lock type) on the exterior side of uilding/structure, upto 25 metre height, above ground level, including additional rows of scaffolding in stepped manner as per requirement of site, made with 40 mm dia M.S. tube, placed 1.5 metre centre to centre, horizontal & vertical tubes joint with cup & lock system with M.S. Tubes, M.S. tube challis, M.S. clamps and staircase system in the scaffolding for working platform etc. and aintaining it in a serviceable condition for execution of work of cleaning and/ or pointing and/ or applying hemical and removing it thereafter. The scaffolding system shall be stiffened with bracings, runners, connecting with the building etc, wherever required, if feasible, for inspection of work at required locations with essential safety features for the workmen etc., complete as per directions and approval of Engineer-in-charge | 125.00 | SQM | 338.25 | 327.00 | 40875.00 | 220.00 | 27500.00 | 300.00 | 37500.00 | 310.00 | 38750.00 | 27500.00 | N.F.LEL CONSTRUCTION
| Total in Figures |  |  |  |  | 4735997.25 |  | 4883533.75 |  | 4070290.50 |  | 4680686.25
Lowest Amount Quoted BY: SADH BUILDERS(4070290.50)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of the Pumps and Pipelines in Pump House from underground sump to overhead tank at EFA Tender ID: 2026_AVNL_280845_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SADH BUILDERS (BID ID -1038845) | 4070290.50 | L1
| 2 | S VINAYAGAMURTHY (BID ID -1038846) | 4680686.25 | L2
| 3 | HARI ENTERPRISES (BID ID -1038791) | 4735997.25 | L3
| 4 | N.F.LEL CONSTRUCTION (BID ID -1041829) | 4883533.75 | L4