## BoQ1
eProcurement System Government of India Created By: Govindarajan Ganesan Created Date/Time: 10-Oct-2026 11:49 AM Tender Title: Repair and maintenance of street light at KLP Thrissur 159 Bn BSF under SHQ BSF Chennai. Tender ID: 2026_BSF_926535_1
Tender Inviting Authority: The Assistant Commandant (Electrical), SHQ BSF Chennai
Name of Work: Repair and Maintenance of street lights at KLP Thrissur 159 Bn BSF under SHQ BSF Chennai.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ELECTROWIND ENGINEERING COMPANY (GSTN-NA) BID ID -3484357 |  | MOHD ANAS (GSTN-NA) BID ID -3485083
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying, Installation, Testing & Commissioning of Street light LED fixture, powder coated pressure die cast aluminium body with built in or separate driver as per the requirement with Driver efficiency >85%, Input voltage: 140-270 Volt AC, frequency 50/60 hz, Operating temp range -5 0C to 50 0C, internal surge protection of 5 KV L,N,E as per IEC 61000-4-5, Driver efficiency >85%,THD < 10% as per IEC 61000-3-2, P. F.≥0.95, IP-66,IK-10, CRI >70, under voltage and over voltage protection, EMI-EMC as per CISPR-15, lenses for beam angle as per IESNA type I/II/III as per the width of the road and the project requirement., suitable to fit in up to 65mm dia pipe, life time (LED, Driver & electrical circuitary) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report, CCT 3000°K / 4000°K / 5700°K /6500°K (As per ANSI Bin) SDCM(Standard Deviation Color Matching) <5, Maximum power consumption should not more than the specified rating and Fixture shall be of relevant BIS standard complete in all respect i/c external connections with 1.5 sq mm FRLS/HFFR, PVC insulated copper conductor single core cable and earthing etc. as required with Minimum 5 year OEM warranty. System lumen efficacy >135 lm/Watt output . LM79 & LM80 Test report and all testing required for LED fixtures as per BIS shall be submitted.. Shape size and CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminium housing such that LED junction temperature shall not rise above 90°C). 50 watt. | 30.00 | Nos. |  | 3065.00 | 91950.00 | 2787.00 | 83610.00 | 83610.00 | MOHD ANAS
2.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. (6 A single pole). | 62.00 | Nos. |  | 380.00 | 23560.00 | 340.00 | 21080.00 | 21080.00 | MOHD ANAS
3.00 | supplying and fixing of 63 A 4 pole MCCB, 415 V AC including all necessary hardware, interconnections,testing and commissioning as required | 2.00 | Nos. |  | 4750.00 | 9500.00 | 4310.00 | 8620.00 | 8620.00 | MOHD ANAS
4.00 | Supplying and fixing 25 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. (25 A Double pole). | 4.00 | Nos. |  | 968.00 | 3872.00 | 875.00 | 3500.00 | 3500.00 | MOHD ANAS
5.00 | Supply and fixing of timer switch/time module 230 V AC,30A single pole 24/7- Day programmable, suitable for automatic street light Control. | 2.00 | Nos. |  | 3520.00 | 7040.00 | 3990.00 | 7980.00 | 7040.00 | ELECTROWIND ENGINEERING COMPANY
6.00 | Providing, fixing, testing and commissioning of 40 A, 3 pole power contactor, AC operated coil having minimum 1 NO+1 NC auxilliary contacts,complete with all mounting accessories,connections,testing and commissioning as required. | 2.00 | Nos. |  | 9200.00 | 18400.00 | 8370.00 | 16740.00 | 16740.00 | MOHD ANAS
7.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation and refilling the trench etc as required, but excluding sand cushioning and protective covering. (lifting of old cable and relaying of defective cable after necessary repair as required). upto 35 sq mm. | 218.00 | Mtr. |  | 345.00 | 75210.00 | 310.00 | 67580.00 | 67580.00 | MOHD ANAS
8.00 | Supplying and laying of 2 core, 25 Sqmm, Aluminum stranded conductor Power Cables, XLPE Insulated,cores laid up, PVC tape innersheathed, Armour galvanised steel strip,extruded PVC Type ST2 sheathed,650/1100V grade as per IS 7098(Part 1) 1988 complete as required. | 20.00 | Mtr. |  | 485.00 | 9700.00 | 435.00 | 8700.00 | 8700.00 | MOHD ANAS
9.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 35 sq. mm | 8.00 | Nos. |  | 3600.00 | 28800.00 | 3400.00 | 27200.00 | 27200.00 | MOHD ANAS
| Total in Figures |  |  |  |  | 268032.00 |  | 245010.00
Lowest Amount Quoted BY: MOHD ANAS(245010.00)

## BOQ Summary
BOQ Summary Details Tender Title: Repair and maintenance of street light at KLP Thrissur 159 Bn BSF under SHQ BSF Chennai. Tender ID: 2026_BSF_926535_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | MOHD ANAS (BID ID -3485083) | 245010.00 | L1
| 2 | ELECTROWIND ENGINEERING COMPANY (BID ID -3484357) | 268032.00 | L2