## BoQ1
Government eProcurement System Created By: Roshan Anurag Dung Dung Created Date/Time: 19-Jun-2026 05:44 PM Tender Title: COMPOSITE WORKS AT SV-18 MHASKAL AND NPL KALYAN Tender ID: 2026_GAIL_273651_1
Tender Inviting Authority: GAIL(India)Limited
Name of Work:Composite Works Including Construction of Civil & Composite Works at SV-18 Mhaskal & NPL Kalyan involving a) Installation of Launcher-Receiver, Pressure Reduction Skid and b) Supply, Installation & Commissioning of all Associated Station Pipings, Valves, Fittings, and Related Instrumentation, Electrical & Civil Works.
Tender Id: GAIL/MU/C&P/O&M/25/C113
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD (GSTN-NA) BID ID -1016104
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | PLANT PIPING (ABOVE GROUND)
2.00 | Complete Carbon Steel Piping Work with painting, including all fittings, flanges, and supply of all required gaskets, studs, bolts & nuts, etc., as described below.
3.00 | Transportation of all piping items from Contractor's storage point to work site; complete work of fabrication, erection, painting, testing of pipes, flanges, and fittings; and making ready for further commissioning/start-up of carbon steel piping of all sizes and ratings, including supply of all consumables, equipment, manpower, and other resources, and execution of, but not limited to, the following works in accordance with relevant specifications indicated in the particular job specification & scope of work indicated in SCC, drawings, specifications, and instructions of EIC, and as per all provisions of the Contract Document.
4.00 | Fabrication including cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, etc., to match with the matching edges of uneven/different thickness wherever required; welding; attachment of all pipe fittings like elbows, tees, reducers; supply of gasket & stud bolts (below 4"), and above 4" shall be paid as per SOR; nuts, U-clamps, etc., as required for completion of job. All fittings installation shall be paid on a linear meter basis under this item only.
5.00 | Handling and installation of all types & sizes of valves, including assembly of valve accessories/actuator (if any) by bolting, threading, or welding; supply and insertion of gaskets, nuts & bolts, nipples, tubing, etc., at all elevations of pipe sleepers, supports, or overhead on racks, equipment nozzles, skid & painting, etc.; supply of all consumables, manpower, equipment, etc., for completion of all works as per scope of work and as per drawings, specifications, and instructions of EIC, including servicing/cleaning of valves wherever required.
6.00 | Installation of weldolets, sockolets, flanges, vent and drain point connections, etc., as required.
7.00 | Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids, and at all elevations, including installation, design & fabrication of all types of supports/jump-over and carrying out connected activities for all types of valves, including supply & fixing of gaskets, studs/bolts, nuts wherever required for all sizes; leveling, aligning, joining of flanges, blind flanges, connecting with equipment nozzles, strainers, tie-in with existing piping/facilities, etc.; tapping for inline instruments like pressure gauges, thermowells, sample connection, etc.
8.00 | Design and Residual Engineering
9.00 | Preparation of bill of material (BOM)
10.00 | Preparation of Construction, Fabrication, GAD, isometric and As-built drawings
11.00 | Carrying out all Non-destructive testing as required except Radiography.
12.00 | Surface preparation before application of primer by means of sand blasting, including supply of approved quality of sand, manpower, machinery, tools & tackles to achieve required roughness as per specification and as per instructions of EIC.
13.00 | Painting of entire system (including aboveground all pipes, fittings, flanges & accessories) suitable for normal corrosive area environment, including supply of approved paints & primers, application of primer & paints, identification lettering/numbering, color-coding, etc., as specified, including rub-down & touch-up of shop primer or scrapping of shop primer wherever required by Company, and providing scaffolding for all heights, etc.
14.00 | Cleaning and flushing by water/compressed air; testing of the systems including hydrostatic, pneumatic, and any other types of testing as specified; draining, drying by compressed air/other methods approved by Company.
15.00 | Precommissioning & making operational all piping systems and equipment.
16.00 | Commissioning Contractor scope shall provide all necessary assistance in terms of supply of manpower, equipment, tools and tackles, required amount of nitrogen for purging of entire terminal piping system including equipment, etc., to the Company during commissioning activities.
17.00 | Completion of all such work in all respects as per scope of work and as per drawings, specifications, and instructions of the Company, and keeping the system ready in all respects for further commissioning and start-up. Proper partition by GI sheet and support for process area and working area shall be done without any extra cost, i.e., no separate reimbursement shall be done for partition. This is required for safety during fabrication works in process area. @Note: For Below 2" Carrying out all Non-destructive testing as required are including in this SOR Items.
18.00 | 2" and below ( Sch-60/Sch-80/Sche160/XXS/XS) | 600.00 | ID |  | 5953.00 | 4214724.00 | 4214724.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
19.00 | Note: For hook-up works at tap-off point, Dispatch & Receiving Terminal, including making provision for hooking up and carrying out shutdown activities at terminals, if necessary, shall be paid as per separate SOR.
20.00 | Above 2" to Below 12" Pipe (Various Thicknes) | 500.00 | ID |  | 6846.00 | 4039140.00 | 4039140.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
21.00 | Plant Piping Above 2" to Below 12" Pipe (Various Thickness – STD, XS, S80)
22.00 | Note: For hook-up works at tap-off point, Dispatch & Receiving Terminal, including making provision for hooking up and carrying out shutdown activities at terminals, if necessary, shall be paid as per separate SOR.
23.00 | INSTALLATION OF VALVES
24.00 | INSTALLATION OF ABOVE GROUND FLANGED VALVES (BALL / PLUG / CHECK / GATE / GLOBE) AS PER DETAILS GIVEN BELOW:
25.00 | Size - 6.0 Inch, Rating - 150#/300#/600# | 2.00 | Nos |  | 10781.00 | 25443.16 | 25443.16 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
26.00 | Size - 2.0 Inch, Rating - 150#/300#/600# | 45.00 | Nos |  | 2969.00 | 157653.90 | 157653.90 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
27.00 | Size - 3/4 Inch, Rating - 150#/300#/600#/800# | 42.00 | Nos |  | 2264.00 | 112203.84 | 112203.84 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
28.00 | INSTALLATION OF ABOVE GROUND BUTT WELDED/SOCKET WELDED VALVES (BALL / PLUG / CHECK / GATE / GLOBE) AS PER DETAILS GIVEN BELOW:
29.00 | Size - 6.0 Inch, Rating - 150#/300#/600# | 3.00 | Nos |  | 12700.00 | 44958.00 | 44958.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
30.00 | Size - 2.0 Inch, Rating -150#/300#/600# | 2.00 | Nos |  | 4234.00 | 9992.24 | 9992.24 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
31.00 | INSTALLATION OF ABOVE GROUND ONE END FLANGED OTHER END BUT WELD VALVES (BALL / PLUG / CHECK / GATE / GLOBE) AS PER DETAILS GIVEN BELOW:
32.00 | Size - 2.0 Inch, Rating - 150#/300#/600# | 4.00 | Nos |  | 4145.00 | 19564.40 | 19564.40 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
33.00 | INSTALLATION OF GOV/ HOV/ ABOVE GROUND GAS ACTUATED VALVES AS PER DETAILS GIVEN BELOW
34.00 | Size - 6 Inch, | 6.00 | Nos |  | 16044.00 | 113591.52 | 113591.52 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
35.00 | SUPPLY OF BENDS
36.00 | Refer the Pipeline Material Specification (PMS), Technical Datasheet for Fittings
37.00 | Thickness shall be matching with the connecting pipes / valves / fittings.
38.00 | Elbow / Bend 90° (Long Radius) 6" BW | 3.00 | Nos. |  | 4200.00 | 14868.00 | 14868.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
39.00 | SUPPLY OF BENDS: ELBOW 90° (Long Radius) 6" D1A ASME B16.9 API 5L GR.X52 8.56MM to be used to achieve 7.1 mm min WT after bending. Technical Specification for Long Radius Bends GAIL-STD-PL-DOC-TS-004 and datasheet GAIL-51-PL-DOC-DS-122.
40.00 | Elbow / Bend 45° (Long Radius) 6" BW | 4.00 | Nos. |  | 2494.00 | 11771.68 | 11771.68 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
41.00 | SUPPLY OF BENDS: ELBOW 45° (Long radius) 6" D1A ASME B 16.9 API 5L GR.X52 8.56MM to be used to achieve 7.1 mm min WT after bending. Technical Specification for Long Radius Bends GAIL-STD-PL-DOC-TS-004 and datasheet GAIL-51-PL-DOC-DS-122.
42.00 | Elbow / Bend 90° (1.5D) 6" BW | 14.00 | Nos. |  | 4200.00 | 69384.00 | 69384.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
43.00 | SUPPLY OF BENDS: ELBOW 90°, 6", 1.5D, BW, D1A, Sch. Matching ASME B 16.9 ASTM A 234 GR. WPB. Refer Piping Material Specification and Technical specification for Seamless Fittings and Flanges GAIL-STD-PI-DOC-TS-003 for details.
44.00 | Elbow / Bend 45° (1.5D) 6" BW | 1.00 | Nos. |  | 2494.00 | 2942.92 | 2942.92 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
45.00 | SUPPLY OF BENDS: BEND 45°, 6", D1A, Schedule Matching, ASME B 16.9 ASTM A 234 GR. WPB. Refer Piping Material Specification and Technical specification for Seamless Fittings and Flanges GAIL-STD-PI-DOC-TS-003 for details
46.00 | Elbow 90° (1.5D) 2" BW | 48.00 | Nos. |  | 854.00 | 48370.56 | 48370.56 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
47.00 | SUPPLY OF BENDS: ELBOW 90°, 2", 1.5D, D1A, Schedule: Matching, ASME B 16.9 ASTM A 234 GR. WPB. Refer Piping Material Specification and Technical specification for Seamless Fittings and Flanges GAIL-STD-PI-DOC-TS-003 for details.
48.00 | Elbow 90° (1.5D) 2" BW LTCS | 10.00 | Nos. |  | 945.00 | 11151.00 | 11151.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
49.00 | SUPPLY OF BENDS: ELBOW 90°, 2", D4A, BW, 1.5D, Schedule: Matching, ASME B 16.9 LTCS ASTM A420 GR. WPL6. Refer Piping Material Specification and Technical specification for Seamless Fittings and Flanges GAIL-STD-PI-DOC-TS-003 for details.
50.00 | Elbow 90° 1" SW LTCS | 4.00 | Nos. |  | 591.00 | 2789.52 | 2789.52 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
51.00 | SUPPLY OF BENDS: ELBOW 90°, 1",6000#,SW, D4A, ASME B 16.11; A350 GR LF2. Refer Piping Material Specification and Technical specification for Seamless Fittings and Flanges GAIL-STD-PI-DOC-TS-003 for details.
52.00 | Elbow 90° 3/4" SW LTCS | 2.00 | Nos. |  | 538.00 | 1269.68 | 1269.68 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
53.00 | SUPPLY OF BENDS: ELBOW 90° 3/4",6000#,SW, D4A, ASME B 16.11; A350 GR LF2. Refer Piping Material Specification and Technical specification for Seamless Fittings and Flanges GAIL-STD-PI-DOC-TS-003 for details.
54.00 | Elbow 90° 3/4" SW | 4.00 | Nos. |  | 499.00 | 2355.28 | 2355.28 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
55.00 | SUPPLY OF BENDS: ELBOW 90°, 3/4", D1A, SW, 6000#, ASME B 16.11 ASTM A 105. Refer Piping Material Specification and Technical specification for Seamless Fittings and Flanges GAIL-STD-PI-DOC-TS-003 for details.
56.00 | Elbow 90° 3" BW | 4.00 | Nos. |  | 1247.00 | 5885.84 | 5885.84 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
57.00 | SUPPLY OF BENDS: ELBOW 90°, 3", BW, 1.5D, A4A, Matching ASME B 16.9 ASTM A420 GR. WPL6. Refer Piping Material Specification and Technical specification for Seamless Fittings and Flanges GAIL-STD-PI-DOC-TS-003 for details.
58.00 | SUPPLY OF PIPES
59.00 | CS Pipes 6" API 5L X-52, 7.1mm Coated | 100.00 | Mtr. |  | 6442.00 | 760156.00 | 760156.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
60.00 | CARBON STEEL (CS) PIPES CS PIPES 6" API 5L X-52, 7.1 mm Thick, 3 LPE Coated. Refer Piping Material Specification and TECHNICAL SPECIFICATION - PIPELINE for details.
61.00 | 6" API 5L X-52, 7.9mm Thick | 30.00 | Mtr. |  | 4363.00 | 154450.20 | 154450.20 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
62.00 | CARBON STEEL (CS) PIPES CS PIPES 6" API 5L X-52, 7.9mm Thick Refer Piping Material Specification and TECHNICAL SPECIFICATION - PIPELINE for details.
63.00 | CS Pipes 2" NB Sch XS API 5L, Gr.B, Seamless, BE / A 106 Gr.B. | 144.00 | Mtr. |  | 989.00 | 168050.88 | 168050.88 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
64.00 | CARBON STEEL (CS) PIPES CS Pipes 2" NB Thickness 6.35 mm, API 5L, Gr.B / A 106 Gr.B, Seamless, Refer Piping Material Specification and TECHNICAL SPECIFICATION - PIPELINE for details.
65.00 | LTCS, Pipes 2" NB Sch XS API 5L, Gr.B, Seamless, A333 GR. 6 | 108.00 | Mtr. |  | 1154.00 | 147065.76 | 147065.76 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
66.00 | Low Temperature CARBON STEEL (LTCS) PIPES 2" NB Thickness 6.35 mm, A333 GR. 6, Seamless, Refer Piping Material Specification and TECHNICAL SPECIFICATION - PIPELINE for details.
67.00 | CS Pipes 1 " NB Sch 160 , A 106 Gr.B. | 12.00 | Mtr. |  | 717.00 | 10152.72 | 10152.72 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
68.00 | CARBON STEEL (CS) PIPES 1" NB Sch 160 , A 106 Gr.B. Refer Piping Material Specification and TECHNICAL SPECIFICATION - PIPELINE for details
69.00 | CS Pipes 3/4 " NB Sch 160 , A 106 Gr.B. | 6.00 | Mtr. |  | 619.00 | 4382.52 | 4382.52 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
70.00 | CARBON STEEL (CS) PIPES 3/4" NB Sch 160 , A 106 Gr.B. Refer Piping Material Specification and TECHNICAL SPECIFICATION - PIPELINE for details.
71.00 | LTCS, Pipes 3/4 " NB Sch 160 , A333 GR. 6 | 16.00 | Mtr. |  | 875.00 | 16520.00 | 16520.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
72.00 | Low Temperature CARBON STEEL PIPES LTCS, Pipes 3/4 " NB Sch 160, A333 GR. 6, Refer Piping Material Specification and TECHNICAL SPECIFICATION - PIPELINE for details.
73.00 | LTCS Pipes 3 " NB Sch Std , A333 GR. 6 | 6.00 | Mtr. |  | 1745.00 | 12354.60 | 12354.60 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
74.00 | Low Temperature CARBON STEEL PIPES LTCS 3 " NB Sch 40 Std, A333 GR. 6, Refer Piping Material Specification and TECHNICAL SPECIFICATION - PIPELINE for details
75.00 | Refer Piping Material Specification and TECHNICAL SPECIFICATION - PIPELINE for details.
76.00 | VALVES
77.00 | SUPPLY OF BALL VALVES
78.00 | Ball Valves 0.75", 800#, SW End + Pup | 34.00 | Nos |  | 4630.00 | 185755.60 | 185755.60 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
79.00 | Supply of Socket Welded end- Female (SW) Ends Ball Valves Valves Size - 0.75 Inch, 800#, Pup Piece 150 mm, SW Ends, Design Standard - BS EN 1SO 17292/API6D/API608, Floating type, Full Bore Ball Valve, Lever Operated. API6D Monogram. Refer the Piping Material Specification, Datasheet and Technical Specification of Ball valves. Seat test at 1.1 times the design pressure using Gas (nitrogen)
80.00 | Ball Valves 0.75", 600#, Flange End | 6.00 | Nos |  | 5659.00 | 40065.72 | 40065.72 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
81.00 | Supply of Flanged end Ball Valves Ball Valves Size - 0.75 Inch, 600#, Flanged Ends, Design Standard - BS EN 1SO 17292/API6D/API608, Floating type, Full Bore Ball Valve, Lever Operated. API6D Monogram. Refer the Piping Material Specification, Datasheet and Technical Specification of Ball valves Seat test at 1.1 times the design pressure using Gas (nitrogen)
82.00 | Ball Valves 0.75", LTCS, 600# Flange End | 2.00 | Nos |  | 6615.00 | 15611.40 | 15611.40 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
83.00 | Supply of Flanged end Ball Valves Ball Valves Size - 0.75 Inch, 600#, LTCS, Flanged Ends, Design Standard - BS EN 1SO 17292/API6D/API608, Floating type, Full Bore Ball Valve, Lever Operated. API6D Monogram. Refer the Piping Material Specification, Datasheet and Technical Specification of Ball valves Seat test at 1.1 times the design pressure using Gas (nitrogen)
84.00 | Ball Valves 2", 600#, BW End + Pup Piece | 2.00 | Nos |  | 140532.00 | 331655.52 | 331655.52 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
85.00 | DIB-2 Double Isolation and Bleed # 2 Upstream side seat uni-directional and Downstream Side seat bidirectional) Supply of Butt Weld + Pup piece end Ball Valves Single body complete welded Ball Valves Size - 2", 600#, Butt Ends + 150 mm Pup piece, Design Standard - BS EN 1SO 17292/API6D/API608, Full Bore Ball Valve, Lever Operated. API6D Monogram. Trunion Mounted. Refer the Piping Material Specification, Datasheet and Technical Specification of Ball valves Seat test at 1.1 times the design pressure using Gas (nitrogen)
86.00 | Ball Valves 2", 600#, Butt + Flange end | 4.00 | Nos |  | 177135.00 | 836077.20 | 836077.20 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
87.00 | DIB-2 Double Isolation and Bleed # 2 Upstream side seat uni-directional and Downstream Side seat bidirectional) Supply of Butt Weld with Pup piece 150 mm one End and Flange End on other side Ball Valves Single body complete welded Ball Valves Size - 2", 600#, Design Standard - BS EN 1SO 17292/API6D/API608, Full Bore Ball Valve, Lever Operated. API6D Monogram.Trunion Mounted Refer the Piping Material Specification, Datasheet and Technical Specification of Ball valves Seat test at 1.1 times the design pressure using Gas (nitrogen)
88.00 | Ball Valves 2", 600#, Flanged End | 27.00 | Nos |  | 338247.00 | 10776549.42 | 10776549.42 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
89.00 | DIB-2 Double Isolation and Bleed # 2 Upstream side seat uni-directional and Downstream Side seat bidirectional) Supply of Flange end Ball Valves Size - 2", 600#, Design Standard - BS EN 1SO 17292/API6D/API608, Full Bore Ball Valve, Lever Operated. API6D Monogram. Trunion mounted Refer the Piping Material Specification, Datasheet and Technical Specification of Ball valves API6D Monogram. Seat test at 1.1 times the design pressure using Gas (nitrogen)
90.00 | Ball Valves 6", 600#, BW End+Pup | 3.00 | Nos |  | 661794.00 | 2342750.76 | 2342750.76 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
91.00 | DIB-2 Double Isolation and Bleed # 2 Upstream side seat uni-directional and Downstream Side seat bidirectional) Supply of Ball Valves Size -6 Inch, 600#, Body-ASTM A 216 GR. WCB, Ball ASTM A 216 Gr.WCB/A105+ 0.003” ENP/SS-316, Seat Ring: SS-316, Full Bore, Butt Weld, ASME B16.25, Pup piece length of 300MM on both side of valve. (Pup-piece API 5L X52, WT 7.9 mm) Design Standard - BS EN 1SO 17292/API6D/API608, Full Bore Ball Valve, Gear Operated, Trunnion Mounted, Sealant point with fitting and valves required at both ends API6D Monogram. Refer the Piping Material Specification, Datasheet and Technical Specification of Ball valves. Seat test at 1.1 times the design pressure using Gas (nitrogen)
92.00 | Ball Valves 6", 600#, Flange End | 1.00 | Nos |  | 692223.00 | 816823.14 | 816823.14 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
93.00 | DIB-2 Double Isolation and Bleed # 2 Upstream side seat uni-directional and Downstream Side seat bidirectional) Supply of Ball Valves Size -6 Inch, 600#, Body-ASTM A 216 GR. WCB, Ball ASTM A 216 Gr.WCB/A105+ 0.003” ENP/SS-316, Seat Ring: SS-316, Full Bore, Flanged End, ASME B16.5, Design Standard - BS EN 1SO 17292/API6D/API608, Full Bore Ball Valve, Gear Operated, Trunnion Mounted, API6D Monogram. Refer the Piping Material Specification, Datasheet and Technical Specification of Ball valves. Seat test at 1.1 times the design pressure using Gas (nitrogen)
94.00 | Refer the Piping Material Specification, Datasheet and Technical Specification of Ball valves. Seat test at 1.1 times the design pressure using Gas (nitrogen)
95.00 | SUPPLY OF GLOBE VALVES
96.00 | Globe Valves 2", 600#, Flange | 7.00 | Nos |  | 73794.00 | 609538.44 | 609538.44 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
97.00 | Supply of Globe Valves Size - 2 Inch, 600#, Flange Ends, Design Standard - BS EN 1SO 15761, BS-1873 & API-602 Refer the Piping Material Specification, Datasheet and Technical Specification of Globe valves. Seat test at 1.1 times the design pressure using Gas (nitrogen)
98.00 | Globe Valves 6", 600#, Flange | 2.00 | Nos |  | 353535.00 | 834342.60 | 834342.60 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
99.00 | Supply of Globe Valves Size - 6 Inch, 600#, Flange Ends, Design Standard - BS EN 1SO 15761, BS-1873 & API-602 Refer the Piping Material Specification, Datasheet and Technical Specification of Globe valves. Seat test at 1.1 times the design pressure using Gas (nitrogen)
100.00 | Refer the Piping Material Specification, Datasheet and Technical Specification of Globe valves. Seat test at 1.1 times the design pressure using Gas (nitrogen)
101.00 | SUPPLY OF PLUG VALVES
102.00 | Plug Valves 1", LTCS, 800#, SW | 2.00 | Nos |  | 37485.00 | 88464.60 | 88464.60 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
103.00 | Supply of Plug Valves as per PMS, Technical Specification, and Data Sheet Plug Valves Size - 1 Inch, LTCS, 800#, 6000, SW Ends with 150mm Pup Piece, Design Standard BS 1873 / BS 5353 / API 599 / API 6D API6D Monogram. Seat test at 1.1 times the design pressure using Gas (nitrogen)
104.00 | Plug Valves 2", LTCS, 600#, Flanged | 6.00 | Nos |  | 191835.00 | 1358191.80 | 1358191.80 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
105.00 | Supply of Plug Valves as per PMS, Technical Specification and Data Sheet Plug Valves Size - 2 Inch, LTCS,600#, Flange Ends, Design Standard BS 1873 / BS 5353 / API 599 / API 6D API6D Monogram. Seat test at 1.1 times the design pressure using Gas (nitrogen)
106.00 | Plug Valves 2", 600#, Flange | 1.00 | Nos |  | 191835.00 | 226365.30 | 226365.30 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
107.00 | Supply of Plug Valves as per PMS, Technical Specification and Data Sheet Plug Valves Size - 2 Inch, 600#, Flange Ends, Design Standard BS 1873 / BS 5353 / API 599 / API 6D. API6D Monogram Seat test at 1.1 times the design pressure using Gas (nitrogen)
108.00 | Plug Valves 2", 600#, Butt + Flange End | 4.00 | Nos |  | 191835.00 | 905461.20 | 905461.20 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
109.00 | Supply of Plug Valves as per PMS, Technical Specification and Data Sheet Plug Valves Size - 2 Inch, 600#, One end flange ends other but weld - But End with Pup piece 150mm, Design Standard BS 1873 / BS 5353 / API 599 / API 6D. API6D Monogram Seat test at 1.1 times the design pressure using Gas (nitrogen)
110.00 | Seat test at 1.1 times the design pressure using Gas (nitrogen)
111.00 | SUPPLY OF BALL VALVES GOOV/HOOV
112.00 | Ball Valve HOOV, 6",600#, Flanged End | 2.00 | Nos |  | 955500.00 | 2254980.00 | 2254980.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
113.00 | DIB-2 Double Isolation and Bleed # 2 Upstream side seat uni-directional and Downstream Side seat bidirectional) Supply of HOOV Actuated Valves as per PMS, Technical Specification,Actuator data sheet, and Data Sheet HOOV Ball Valves, Size - 6 Inch, 600#, Body-ASTM A 216 GR. WCB, Ball- ASTM A105 + 0,003" ENP/SS316, Seat Ring: AISI 4140+0.003" ENP, Full Bore, Flanged End, Trunnion Mounted, ASME B 16.5 ENP, Design STD: ISO 17292 / API 6D / API 608 Sealant Injection Point both side API 6D monogram, Above Ground, Hydraulic actuated, including tubing, fitting & associated materials etc. Seat test at 1.1 times the design pressure using Gas (nitrogen)
114.00 | Supply of GOOV Actuated Valves as per Tender
115.00 | Ball Valve GOOV,6",600#,BW End Single Pc | 4.00 | Nos |  | 2690100.00 | 12697272.00 | 12697272.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
116.00 | DIB-2 Double Isolation and Bleed # 2 Upstream side seat uni-directional and Downstream Side seat bidirectional) Single pieces design (no body flange / bolting allowed) Supply of GOOV Actuated Valves as per PMS, Technical Specification, Actuator data sheet and Data Sheet GOOV Ball Valves Size - 6 Inch, 600#, Body-ASTM A 216 GR. WCB, Ball- ASTM A105 + 0,003" ENP/SS316, Seat Ring: AISI 4140+0.003" ENP, Full Bore, End Butt Welded pup piece length of 300MM on both side of valve. (Pup-piece API 5L X52, WT 7.9 mm) (ASME B 16.5 & ASME B16.25), Trunnion Mounted, Above Ground, Gas actuated, including tubing, fitting & associated materials etc. Also refer to the TENTATIVE INSTRUMENTATION CABLE SCHEMATIC: DRAWING NO. MUM-01-4000007328-016-02 and DRAWING NO. MUM-01-4000007328-016-NPL-WIRING Rev 0 Design STD: ISO 17292 / API 6D / API 608 Sealant Injection Point both side Seat test at 1.1 times the design pressure using Gas (nitrogen) API 6D monogram
117.00 | SUPPLY OF PSV
118.00 | PSV 2"x3", 600# x 150#, Flanged End | 2.00 | Nos |  | 66150.00 | 156114.00 | 156114.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
119.00 | PSV 2" 600# x 3" 150#, Refer Technical Specification, Datasheet, Piping Material Specification. Size shall be finalized by Vendor during Engineering.
120.00 | SUPPLY OF FLANGES / BLIND FLANGES
121.00 | Supply of SW Raised Face (SWRF)/WNRF Flanges as per details below:
122.00 | Flange, 6", 600#, Weld Neck | 18.00 | Nos |  | 12469.00 | 264841.56 | 264841.56 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
123.00 | Supply of WNRF Flanges as per details below: WN FLANGE, MATERIAL: A105 (Charpy), RAISE FACE, END FACING SURFACE: 125AARH, NOMINAL PIPE SIZE: 6 IN, PRESSURE RATING: 600#,WALL THICKNESS: 7.9 MM / Matching. Refer Piping material specification, Datasheet for Fitting and Technical Specification for Fittings
124.00 | Flange, 2", 600#, Weld Neck | 70.00 | Nos |  | 3806.00 | 314375.60 | 314375.60 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
125.00 | Supply of WNRF Flanges as per details below: FLANGE, WELDING-NECK,MATERIAL: CARBON STEEL A105 (charpy, END FACING: RAISE FACE,END FACING SURFACE: 125AARH,NOMINAL PIPE SIZE: 2 IN,PRESSURE RATING: 600#, WALL THICKNESS: Matching Refer Piping material specification, Datasheet for Fitting and Technical Specification for Fittings
126.00 | Flange, 2", LTCS, 600#, Weld Neck | 16.00 | Nos |  | 4200.00 | 79296.00 | 79296.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
127.00 | Supply of WNRF Flanges as per details below: FLANGE, WELDING-NECK,MATERIAL: CARBON STEEL,MANUFACTURING PROCESS: FORGED, MATERIAL SPECIFICATION: ASTM A350 LF2,END FACING: RAISE FACE,END FACING SURFACE: 125AARH,NOMINAL PIPE SIZE: 2 IN,PRESSURE RATING: 600,WALL THICKNESS: Matching Refer Piping material specification, Datasheet for Fitting and Technical Specification for Fittings.
128.00 | Flange, 1", LTCS, 600#, SW | 4.00 | Nos |  | 1247.00 | 5885.84 | 5885.84 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
129.00 | Supply of SW Raised Face (SWRF) Flanges as per details below: FLANGE, WELDING-NECK,MATERIAL: CARBON STEEL,MANUFACTURING PROCESS: FORGED, MATERIAL SPECIFICATION: ASTM A350 LF2 Cl. 1,END FACING: RAISE FACE,END FACING SURFACE: 125AARH,NOMINAL PIPE SIZE: 1 IN,PRESSURE RATING: 600,WALL THICKNESS: MATCHING Refer Piping material specification, Datasheet for Fitting and Technical Specification for Fittings.
130.00 | Flange, 3/4", 600#, SW | 32.00 | Nos |  | 1181.00 | 44594.56 | 44594.56 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
131.00 | Supply of SW Raised Face (SWRF) Flanges as per details below: FLANGE, Socket Weld,MATERIAL: CARBON STEEL,MANUFACTURING PROCESS: FORGED, MATERIAL SPECIFICATION: ASTM A105, END FACING: RAISE FACE,END FACING SURFACE: 125AARH,NOMINAL PIPE SIZE: 3/4 IN,PRESSURE RATING: 600,WALL THICKNESS: MATCHING Refer Piping material specification, Datasheet for Fitting and Technical Specification for Fittings.
132.00 | Flange, 3/4", LTCS, 600#, SW | 4.00 | Nos |  | 1247.00 | 5885.84 | 5885.84 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
133.00 | Supply of SW Raised Face (SWRF) Flanges as per details below: FLANGE, SOCKET WELD,MATERIAL: CARBON STEEL,MANUFACTURING PROCESS: FORGED, MATERIAL SPECIFICATION: ASTM A350 LF2,END FACING: RAISE FACE,END FACING SURFACE: 125AARH,NOMINAL PIPE SIZE: 3/4 IN,PRESSURE RATING: 600,WALL THICKNESS: MATCHING Refer Piping material specification, Datasheet for Fitting and Technical Specification for Fittings.
134.00 | Flange, 3", LTCS, 150#, Weld Neck | 4.00 | Nos |  | 4066.00 | 19191.52 | 19191.52 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
135.00 | Supply of WNRF Flanges as per details below: FLANGE, WELDING-NECK,MATERIAL: CARBON STEEL,MANUFACTURING PROCESS: FORGED, MATERIAL SPECIFICATION: ASTM A350 LF2,END FACING: RAISE FACE,END FACING SURFACE: 125AARH,NOMINAL PIPE SIZE: 3 IN,PRESSURE RATING: 150,WALL THICKNESS: MATCHING Refer Piping material specification, Datasheet for Fitting and Technical Specification for Fittings.
136.00 | Supply of Raised Face Blind Flanges (BLRF) as per details given below:
137.00 | Flange, Blind, 6", 600# | 1.00 | Nos |  | 10762.00 | 12699.16 | 12699.16 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
138.00 | Supply of Raised Face Blind Flanges (BLRF) Size - 6 Inch, 600# , Material - ASTM A105, Face/Finish - RF/125AARH , Dimn. Std. ASME B16.5 Refer Piping material specification, Datasheet for End Flanges and Technical Specification for Fittings.
139.00 | Flange, Blind, 2", 600# | 10.00 | Nos |  | 1903.00 | 22455.40 | 22455.40 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
140.00 | Supply of Raised Face Blind Flanges (BLRF) Size - 2.0 Inch, 600# , Material - ASTM A105, Face/Finish - RF/125AARH , Dimn. Std. ASME B16.5 Refer Piping material specification, Datasheet for End Flanges and Technical Specification for Fittings.
141.00 | Flange, Blind, 3/4", 600# | 6.00 | Nos |  | 1247.00 | 8828.76 | 8828.76 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
142.00 | Supply of Raised Face Blind Flanges (BLRF) Size - 3/4 Inch, 600# , Material - ASTM A105, Face/Finish - RF/125AARH , Dimn. Std. ASME B16.5 Refer Piping material specification, Datasheet for End Flanges and Technical Specification for Fittings.
143.00 | Flange, Blind, 3/4", LTCS, 600# | 2.00 | Nos |  | 1339.00 | 3160.04 | 3160.04 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
144.00 | Supply of Raised Face Blind Flanges (BLRF) Size - 3/4 Inch, 600# , Material - ASTM A350 GR. LF2, Face/Finish - RF/125AARH , Dimn. Std. - ASME B16.5 Refer Piping material specification, Datasheet for End Flanges and Technical Specification for Fittings.
145.00 | SUPPLY OF TEES, SOCKOLET, WELDOLET
146.00 | Supply of BW Equal Tee as per details given below:
147.00 | Tee, Equal, 6", BW | 3.00 | Nos |  | 5906.00 | 20907.24 | 20907.24 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
148.00 | Supply of BW Equal Tee; Size - 6 Inch, TEE, EQUAL,MATERIAL: CARBON STEEL,MATERIAL SPECIFICATION: MSS SP 75 GR. WPHY-70 ,CLASS:, END CONNECTION: BUTT WELD,6 NB EQUAL TEE CS SMLS BW ASTM A234 GR. WPB ASME B16.9 TO MATCH 6 INCH 7.9 MM WT API 5L X52 / Matching Refer Piping material specification, Datasheet for Fittings and Technical Specification for Fittings.
149.00 | Tee, Equal, 2", BW | 9.00 | Nos |  | 1706.00 | 18117.72 | 18117.72 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
150.00 | Supply of BW Equal Tee Size - 2 Inch, Thk/Sch - XS, Material - ASTM A 234 gr WPB, Dimn. Std. - ASME B 16.9. Refer Piping material specification, Datasheet for Fittings and Technical Specification for Fittings.
151.00 | Tee, Equal, 3/4", SW | 2.00 | Nos |  | 722.00 | 1703.92 | 1703.92 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
152.00 | Supply of Equal Tee Size - 3/4 Inch, Thk/Sch - Matching, Material - ASTM A 105, 6000# Dimn. Std. - ASME B 16.11, SW Refer Piping material specification, Datasheet for Fittings and Technical Specification for Fittings.
153.00 | Supply of BW Un-equal Tee as per details given below:
154.00 | Tee, Unequal, 2" x 1", BW | 2.00 | Nos |  | 1509.00 | 3561.24 | 3561.24 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
155.00 | Supply of BW Un-equal Tee 2" x 1", UNEQUAL TEE, ASTM A 234 gr WPB, SMLS, ASME B16.9, BW, R=1.5D, Thickness Matching Refer Piping material specification, Datasheet for Fittings and Technical Specification for Fittings.
156.00 | Tee, Unequal, 2" x 3/4", BW, LTCS | 2.00 | Nos |  | 1509.00 | 3561.24 | 3561.24 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
157.00 | Supply of BW Un-equal Tee 2" x 3/4" UNEQUAL TEE, ASTM A 420 GR.WPL6, SMLS, ASME B16.9, BW, R=1.5D Refer Piping material specification, Datasheet for Fittings and Technical Specification for Fittings.
158.00 | Tee, Unequal, 2" x 3/4", BW | 14.00 | Nos |  | 1509.00 | 24928.68 | 24928.68 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
159.00 | Supply of BW Un-equal Tee 2" 3/4", UN EQUAL TEE, ASTM A234 GR.WPB-W, SMLS, BW, ASME B16.9 Refer Piping material specification, Datasheet for Fittings and Technical Specification for Fittings.
160.00 | Tee, Unequal, 2" x 1", BW, LTCS | 2.00 | Nos |  | 1837.00 | 4335.32 | 4335.32 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
161.00 | Supply of BW Un-equal Tee 2" x 1" UNEQUAL TEE, ASTM A 420 GR.WPL6, SMLS, ASME B16.9, BW, R=1.5D Refer Piping material specification, Datasheet for Fittings and Technical Specification for Fittings.
162.00 | Supply of Sockolet conforming to MSS-SP-97, Material - ASTM A105 and as per details given below:
163.00 | 6" x 3/4", 6000# | 5.00 | Nos |  | 2165.00 | 12773.50 | 12773.50 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
164.00 | Supply of Sockolet conforming to MSS-SP-97, Material - ASTM A105 and as per details given below: Supply of Sockolet conforming to MSS-SP-97, Material - ASTM A105; 6" x 3/4", 6000# Refer Piping material specification, Datasheet for Fittings and Technical Specification for Fittings.
165.00 | Supply of Weldolet conforming to MSS-SP-97, Material - ASTM A105 (CHARPY) and as per details given below:
166.00 | Weldolet, 6"x 2", 6000# | 17.00 | Nos |  | 3334.00 | 66880.04 | 66880.04 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
167.00 | Supply of Weldolet conforming to MSS-SP-97, Material - ASTM A105 (CHARPY) and as per details given below: 6" x 2", Thk/Sch - Matching, 6000#, But Weld Refer Piping material specification, Datasheet for Fittings and Technical Specification for Fittings.
168.00 | SUPPLY & INSTALLATION OF QOEC
169.00 | QOEC 2"- 600 # | 2.00 | Nos. |  | 472500.00 | 1115100.00 | 1115100.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
170.00 | Supply and Installation of QOEC for ventline including all necessary piping fabrication works, including providing all necessary equipments, labour, materials, consumables and inputs other than Owner supplied materials and per forming all works as per drawings, data sheet, specifications enclosed with the Contract and directions of Engineer-in- Charge. QUICK OPENING END CLOSURE - QOEC 2", 600#. Refer Piping material specification, Datasheet for QOEC and Technical Specification for QOEC.
171.00 | Nipple
172.00 | Nipple 3/4 inch, ASTM-106, Sch XXS | 5.00 | Nos |  | 1444.00 | 8519.60 | 8519.60 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
173.00 | Supply of Nipple 3/4 inch, ASTM-106, Sch- XXS ( One side Threaded (NPT)-Male, One side socket welded)- Length : 150MM Refer Piping material specification, Datasheet for Fittings and Technical Specification for Fittings.
174.00 | Supply of Flow Tee as per tender
175.00 | FLOW TEE, EQUAL, 6" | 2.00 | Nos. |  | 20475.00 | 48321.00 | 48321.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
176.00 | FITTING, FLOW TEE, EQUAL,MATERIAL: CARBON STEEL,MANUFACTURING PROCESS: , MATERIAL SPECIFICATION: MSS SP # 75 Gr. WPHY 52, GRADE: ,CLASS: 600#,END CONNECTION: BW, FLOW TEE, EQUAL,MAIN LINE: 6IN , BRANCH LINE: 6 IN,CLASS: 600, APLI 5L X-52 7.9 mm Refer Piping material specification, Datasheet for Flow Tee and Technical Specification for Flow Tee.
177.00 | Supply of Specticle Blind as per tender
178.00 | Spectacle Blind, 6", 600# | 2.00 | Nos. |  | 21525.00 | 50799.00 | 50799.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
179.00 | Supply of Specticle Blind as per tender Size - 6.0 Inch, 600# , Material - ASTM A105, Face/Finish - RF/125AARH , Dimn. Std. - ASME B 16.48 Refer Piping material specification, Datasheet for Sp. Blinds and Technical Specification for Sp. Blinds.
180.00 | Spectacle Blind, 2", 600# | 27.00 | Nos. |  | 3281.00 | 104532.66 | 104532.66 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
181.00 | Supply of Specticle Blind as per tender Size - 2.0 Inch, 600# , Material - ASTM A105, Face/Finish - RF/125AARH , Dimn. Std. - ASME B 16.48 Refer Piping material specification, Datasheet for Sp. Blinds and Technical Specification for Sp. Blinds.
182.00 | Spectacle Blind, 1", 600# | 2.00 | Nos. |  | 2047.00 | 4830.92 | 4830.92 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
183.00 | Supply of Specticle Blind as per tender Size - 1.0 Inch, 600# , Material - ASTM A105, Face/Finish - RF/125AARH , Dimn. Std. - ASME B 16.48 Refer Piping material specification, Datasheet for Sp. Blinds and Technical Specification for Sp. Blinds.
184.00 | Spectacle Blind, 3/4", 600# | 4.00 | Nos. |  | 1575.00 | 7434.00 | 7434.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
185.00 | Supply of Specticle Blind as per tender Size - 3/4 Inch, 600# , Material - ASTM A105, Face/Finish - RF/125AARH , Dimn. Std. - ASME B 16.48 Refer Piping material specification, Datasheet for Sp. Blinds and Technical Specification for Sp. Blinds.
186.00 | Supply of Insulating Joints as per tender
187.00 | Size - 6 Inch, 600#, Insulating Joints | 3.00 | Nos. |  | 111543.00 | 394862.22 | 394862.22 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
188.00 | Refer Piping material specification, Datasheet for Insulating Joints and Technical Specification for Insulating Joints.
189.00 | Supply of Stud bolt with 02 nuts as per details given below:
190.00 | Stud with 2 nuts for 6"x 600# Flange | 20.00 | Set |  | 6142.00 | 144951.20 | 144951.20 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
191.00 | Supply of Stud with 2 nuts for 6"x 600# Flange as per details given below: 6" D1A ASME B18.2, STUD: ASTM A193 GR.B7; NUT: ASTM A194 GR.2H STUD: CONTINUOUS/FULL THREAD, HEADLESS, 1" x 172 mm LONG NUT: HEXAGONAL. Set means complete number of stud and nut required for 1 flange
192.00 | Stud with 2 nuts for 6"x 600# Flange | 4.00 | Set |  | 6772.00 | 31963.84 | 31963.84 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
193.00 | Supply of Stud with 2 nuts for 6"x 600# Flange as per details given below: 6" D1A ASME B18.2, STUD: ASTM A193 GR.B7; NUT: ASTM A194 GR.2H STUD: CONTINUOUS/FULL THREAD, HEADLESS, 1" x 210 mm LONG NUT: HEXAGONAL. Set means complete number of stud and nut required for 1 flange
194.00 | Supply of spiral-wound gasket as per details given below:
195.00 | Gasket for 6" 600# SS Ring | 22.00 | Nos. |  | 718.00 | 18639.28 | 18639.28 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
196.00 | Supply of Gasket for 6" 600# SS Ring 6", D1A, ASME B16.20 & ASME B16.5 SS-316 WINDING + GRAPHITE FILLER WITH STAINLESS STEEL INNER & OUTER RINGS
197.00 | RADIOGRAPHY
198.00 | Performance of radiographic inspection by gamma radiation as per scope of work and as per specifications in piping of all types and thickness including providing / hiring of all necessary equipments, supply of all consumables, and whatever else even though not expressly mentioned but required to perform the work as per specifications and instructions of EIC (full circle re-radiography of the repaired joint and additional radiography necessitated due to poor performance of contractor's welder shall be carried out by the Contractor at his own cost and shall not be paid extra by Company). Radiographs shall be submitted to the EIC for acceptance whose decision shall be final and binding.
199.00 | Radiography up to 2" NB | 220.00 | Each |  | 1890.00 | 490644.00 | 490644.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
200.00 | Radiography above 2" to 06" NB | 100.00 | Each |  | 8022.00 | 946596.00 | 946596.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
201.00 | TRANSPORTATION
202.00 | This SOR is only applicable for any GAIL supplied items shifting from GAIL site / store or Handover items after project completion shifting to GAIL store / site.
203.00 | RECEIVING & TAKING OVER, HANDLING, TRANSPORTATION OF PIPES , FLANGES , FITTINGS , VALVES/ FILTERING/ METERING SKIDS/PRS /PIG TRAPS & OTHER EQUIPMENTS ETC (TERMINAL / MAINLINE MATERIAL / SURPLUS MATERIAL) - ANYWHERE IN INDIA
204.00 | The Contractor shall receive and take over, Handling including lifting, Owner-supplied bare / 3 LPE Coated line pipe / Ball Valves ,Flanges , Fittings, filtering, metering, prs skid, pig traps and any other material from GAIL's designated store, inspection of material at dispatch point as well as destination point and its transportation to work-site (including transit insurance) / return of project surplus / sparable material from Project site / Contractor's store to GAIL's store / warehouse including loading on trucks / trailers, transportation, unloading & stacking on wooden sleepers at Contractor's own stock-yard near work-site(s) / GAIL store (as applicable), including arrangement of truck / trailers / cranes / other material / machinery / manpower / consumables.
205.00 | Transportation by Trailer Fix up to 0-50 KM (Weight up to 18 Ton) per trip | 3.00 | Nos |  | 45937.00 | 162616.98 | 162616.98 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
206.00 | Transportation by Truck Fix up to 0-50 KM (Weight up to 10 Ton) per trip | 5.00 | Nos |  | 32812.00 | 193590.80 | 193590.80 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
207.00 | Transportation by Trailer Capacoty 18 Ton (40' L X 8.6' W X 7' H) Beyond 50 KM in addition to SOR Item No. B003701. | 1000.00 | Per KM |  | 79.00 | 93220.00 | 93220.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
208.00 | Transportation by Truck (Weight up to 10 Ton) Beyond 50 KM in addition to SOR Item No. B003702. | 1000.00 | Per KM |  | 53.00 | 62540.00 | 62540.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
209.00 | Note: (1) Transportation up to 50KM shall be paid by SOR no. B003701/B003702. Beyond 50KM transportation shall be paid by SOR no. B003703/B003704. (2) The nominal quantity of pipes, fittings and valves must be accommodated with other material like M-skid, PRS, Pig Launcher / receiver etc. if feasible. (3) The quantities given in above item no. are tentative only and shall not be considered to be binding. The quantities may be increased, decreased or deleted as per the actual site requirement and instructions / recommendations of Owner. The unit rate shall be operated to work out the final payment to the Contractor; (4) Above price shall be exclusive GST but inclusive of all type of toll taxes & duties, transit insurance during transportation & other insurance, etc. including all financial & commercial implication as per the tender document. (5) The weightage of material may be varies as part load or full load as per the project requirement, Bidder to be quoted the price accordingly.
210.00 | FIRE AND SAFETY
211.00 | FIRE EXTINGUISHERS (Portable as per IS 15028)
212.00 | 10 kg capacity DCP fire extinguisher (portable) considered 1 no. for each locations | 15.00 | No. |  | 12887.00 | 228099.90 | 228099.90 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
213.00 | 75 kg DCP (Dry Chemical Powder) fire extinguisher typically has a capacity of 75 kg of dry chemical powder, Fire rating 233B | 3.00 | No. |  | 73057.00 | 258621.78 | 258621.78 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
214.00 | HOOK UP ACTIVITY
215.00 | HOOK UP ACTIVITY 6 inch with the existing Pipeline.
216.00 | Hook-up works at tap-off point, Despatch and Receiving Terminal including making provision for hooking up and carrying out shutdown activities at terminals if necessary
217.00 | Carbon Steel Piping Work with painting
218.00 | Transportation of all piping items from Contractor's storage point to work site complete work of fabrication, erection, painting, testing and making ready for further commissioning / start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, the following works in accordance with relevant specifications indicated in particular job specification & scope of work indicated in SCC, drawings, specification and instructions of EIC and as per all provisions of the Contract Document.
219.00 | Fabrication including cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, etc. to match with the matching edges of uneven / different thickness wherever required, welding, attachment of all pipe fittings including supply of all consumables required for completion of job.
220.00 | Supply of all manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of EIC wherever required. Preparation of Construction, Fabrication, isometric and As-built drawings.Carrying out Non-destructive testing as required except Radiography.
221.00 | Surface preparation before application of primer by means of sand blasting including supply of approved quality of sand, manpower, machineries, tools & tackles to achieve required roughness as per specification and as per instruction of EIC.
222.00 | Testing/Golden Tie -In with existing Pipeline
223.00 | Precommissioning & making operational all piping system and equipments.
224.00 | Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start-up.
225.00 | Piping different grades & thickness | 60.00 | Inch- Dia |  | 32812.00 | 2323089.60 | 2323089.60 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
226.00 | INSTALLATION
227.00 | INSTALLATION OF FILTERING/ METERING/ PRS SKID/ ANALYZER AND SCRAPER TRAPS
228.00 | Installtion of above ground owner supplied Filtering , Metering , PRS Skid, Analyzer, Pig traps and other equipment at work site up to mechanical completition in all respect, inclusive of painting suitable for Normal Corrosive Environment at all elevation , fixing of foundation bolts, welding wherever required, aligning, grouting, hooking-up, enabling works as required and completing in all respect as per drawings, specification and instruction of EIC. Contractor scope also include to provide commissioning assitance during pre-commissing / commissioning of filtering skid/metering skid /PRS/pig trap and other equipments. Note: Instalation and commssioning of Instrumentation items such as Gas Chromatograph (GC) & metering panel(flow computer panel), cable laying are seperately covered under Instrumentation SOR
229.00 | Note: Instalation and commssioning of Instrumentation items such as Gas Chromatograph (GC) & metering panel(flow computer panel), cable laying are seperately covered under Instrumentation SOR
230.00 | Installation of Pig Scraper trap | 2.00 | No |  | 328125.00 | 774375.00 | 774375.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
231.00 | Installation of above ground Flanged/ Welded Scraper Traps up to mechancial completion in all respectinclusive of painting suitable for Normal Corrosive Environment
232.00 | Installation of Filtering / PRS | 1.00 | No |  | 420000.00 | 495600.00 | 495600.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
233.00 | Installation of above ground Filtering/ Metering/ Pressure Reducing Skid up to mechanical completion in all respect inclusive of painting suitable for Normal Corrosive Environment at various locations.
234.00 | DISMANTLING AND CLEARING OF FILTERING/ METERING/ PRS SKID / SCRAPER TRAPS & OTHER EQUIPMENTS
235.00 | Dismantling and Clearing of old (presently installed) Skid / Scraper Traps and or other Equipments, as per instruction of EIC. Contractor scope also include to provide necessary manpower, equipments & machinery for the above work. | 5.00 | Ton |  | 42000.00 | 247800.00 | 247800.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
236.00 | PADDING FOR PIPE SUPPORTS (4 Inch and Above)
237.00 | Preparation, Fabrication and erection of padding of circle for pipe supports (for all sizes/ thickness). Welding shall be done by approved welder as per Approved WPS of Station piping with Root 6010 & Hot pass 7018 . | 900.00 | RM |  | 1968.00 | 2090016.00 | 2090016.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
238.00 | NITROGEN SUPPLY
239.00 | Supply of Nitrogen | 800.00 | m3 |  | 761.00 | 718384.00 | 718384.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
240.00 | Supply of Nitrogen for preservation of Pipeline/ purging of pipeline / hookup & shut down activities . Along with Vaporiser of sufficient Capacity. i.e 500 SCM/hr
241.00 | INSTALLATION OF EQUIPMENT OTHER THAN ITEM NUMBER B004000
242.00 | Installtion of above ground owner supplied equipment other than listed in item No B004000 at work site up to mechanical completition in all respect, inclusive of painting suitable for Normal Corrosive Environment at all elevation , fixing of foundation bolts, welding wherever required, aligning, grouting, hooking-up, enabling works as required and completing in all respect as per drawings, specification and instruction of EIC. Contractor scope also include to provide commissioning assitance during pre-commissing / commissioning of equipments | 10.00 | Ton |  | 52920.00 | 624456.00 | 624456.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
243.00 | Note: (1) The quantities given above against individual items are indicative and shall not be considered to be binding. The quantities may be increased, decreased or deleted at site at the time of actual execution. Procurement shall be done as per actual site condition, approved construction drawings and as per instruction of EIC. The unit rate shall be operated to work out the final payment to the contractor; (2) In each area, quantities given against individual item may be utilised / used for other consumers in same area.
244.00 | SECTION-C [CIVIL / STRUCTURAL & ARCHITECTURAL]
245.00 | GEO TECHNICAL INVESTIGATION | 2.00 | each |  | 262500.00 | 619500.00 | 619500.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
246.00 | Conducting soil investigation with boring of minimum150mm dia. boreholes of maximum 10m depth including all field tests and laboratory tests, mobilization and demobilization of equipments & personnel etc. for soil investigation for each borehole location . complete work in all respects as per drawings, specifications and directions of Engineer-in-Charge including submitting hard copies of Reports & recommendations and supply of electronic files.
247.00 | SAND FILLING | 85.00 | M3 |  | 3748.00 | 375924.40 | 375924.40 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
248.00 | Supplying and filling approved SAND of specified quality under floors, in foundations, plinths, tank foundations etc. for all depths and heights including cost of sand,royalties, transportation to site for all leads and lifts,including loading, unloading, spreading in layers of loose thickness not exceeding 150 mm,watering,ramming,compacting with mechanical compactors and/or other equipment to the specified levels to achive 85% relative density as per IS:2720 Part XIV,including preparation of subgrade to the required slope,providing testing apparatus and testing the degree of consolidation all complete as per drawings, specifications and direction of Engineer-in-charge.The rates shall be inclusive of the cost of all labour,material,equipments etc. all complete .
249.00 | DEMOLITION OF R.C.C./BRICKS/STONE MASONRY/STEEL WORK
250.00 | Site clearance by demolition of R.C.C./Brickwork/Stone Masonry/Stone Soling, Flexible pavements etc. along with removing the debris and disposal of unserviceable material to any lead and staking of serviceable materials, handing over serviceable material to concerned department if required as per technical specifications and direction of Engineer-in-charge. Note: 1. Rate includes cost of all labour, tools, tackles, hire charges, royalties, levies, leads, loading/unloading, transportation, water, electric power, illumination etc. complete in all respects as per scope of work, detailed construction drawings, technical specifications and direction of Engineer-in-charge. 2. Demolition of RCC/PCC/Brick Masonry/Road will be paid in NET CUM as demolished. | 66.00 | M3 |  | 4704.00 | 366347.52 | 366347.52 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
251.00 | Site clearance by demolition of STEEL work etc. along with removing the disposal of unserviceable material to any lead and staking of serviceable materials, handing over serviceable material to concerned department if required as per technical specifications and direction of Engineer-in-charge. Note: 1. Rate includes cost of all labour, tools, tackles, hire charges, royalties, levies, leads, loading/unloading, transportation, water, electric power, illumination etc. complete in all respects as per scope of work, detailed construction drawings, technical specifications and direction of Engineer-in-charge. 2. Demolition of steel work will be paid in NET Kg as demolished. | 2000.00 | Kg |  | 53.00 | 125080.00 | 125080.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
252.00 | ERC/IRC
253.00 | Construction of ERC/IRC as per Std. including supplying and laying in position PVC pipes conforming to IS:4985 Class-I for electrical and instrumentation Road Crossings as per standard drawing and its addendum, including cutting the pipes if necessary, lowering, laying in position to proper levels, etc. embedded in M-20 grade concrete, providing proper jointing as per code requirements or manufacturer's recommendations, etc. including earth work in excavation in all types of soil except soft and hard rock, backfilling and making good the surface, including cutting of new/ existing roads and making good the same including supply of any road material if required, (Back filling with road material shall be done in 150 mm thick layers well watered and compacted), including supplying and providing in the encasement concrete, cable crossing indicator made out of 4 mm thick MS circular plate of dia. 150mm welded to 16 mm dia. MS rod of approximately 1.0 m length and painting and lettering with 2 coats of approved enamel paint of approved colour over a coat of red oxide primer etc., supply and fixing of reinforcement as per drawing, including disposal of surplus earth anywhere within plant boundary limit etc. all complete as per drawings, specifications and instructions of Engineer-in-Charge. | 25.00 | M |  | 26460.00 | 780570.00 | 780570.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
254.00 | EARTH WORK IN FOUNDATION
255.00 | Earth work in Excavation below ground level for all kinds of works in ALL TYPES OF SOIL as classified in specification for a depth upto 1.5m including removal of vegetation, shrubs and debris, cutting and dressing of sides in slopes, levelling, grading and ramming of bottoms, dewatering of accumulated water from any source and keeping the surface dry for subsequent works and disposal or stacking of excavated material within a lead of 100m, as directed including providing temporary supports to existing service lines like water pipes, sewage pipes, electric overhead and underground cables etc. all complete. | 220.00 | M3 |  | 1837.00 | 476885.20 | 476885.20 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
256.00 | For depth beyond 1.5m and upto & inclusive of 3.0m. | 100.00 | M3 |  | 2352.00 | 277536.00 | 277536.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
257.00 | Backfilling after execution of the WORK to proper grade and level with selected materials from available excavated soil from spoil heaps, including re-excavating the deposited soil excavated earlier, breaking clods, laying at all depths and heights in layers of thickness not exceeding 15 Cms. watering, rolling and ramming by manual methods/ mechanical compactors to achieve 90% laboratory maximum dry density, dressing, trimming etc. in foundations, plinths, trenches, pits etc. all complete. | 60.00 | M3 |  | 661.00 | 46798.80 | 46798.80 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
258.00 | Transporting and disposing the SURPLUS EARTH AND DEBRIS including shrubs and vegetations from construction area beyond the initial lead of 100M including re-excavating the deposited soil excavated earlier, transportation, loading, unloading, laying at all depths and heights, stacking, levelling and dressing both the area (viz. from where the earth is transported and where it is deposited) to required levels and slopes complete with all lifts as directed. For carting on the basis of truck measurements (volume of truck reduced by 30% for voids) i) Upto 1.0Km. | 160.00 | M3 |  | 470.00 | 88736.00 | 88736.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
259.00 | PLAIN & REINFORCED CEMENT CONCRETE:
260.00 | Providing and laying PLAIN CEMENT CONCRETE for all depths below and upto plinth level in foundations,drains, fillings, non-suspended floors, pavements & ramps or any other works etc. including shuttering, tamping, ramming, vibrating, curing, shuttering etc. all as specified in any shape, position, thickness and finishing the top surface rough or smooth as specified and directed all complete for concrete of nominal mix 1:4:8 by volume (1 Cement: 4 Coarse Sand: 8 Crushed Stone Aggregates/Gravels with 40mm and down size graded crushed stone aggaregates. | 50.00 | M3 |  | 11025.00 | 650475.00 | 650475.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
261.00 | Providing and laying PLAIN CEMENT CONCRETE for all depths below and upto plinth level in foundations,drains, fillings, non-suspended floors, pavements & ramps or any other works etc. including shuttering, tamping, ramming, vibrating, curing, etc. all as specified in any shape, position, thickness and finishing the top surface rough or smooth as specified and directed all complete for concrete grade M20 with 20mm and down size graded crushed stone aggaregates/Gravels. . | 10.00 | M3 |  | 11466.00 | 135298.80 | 135298.80 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
262.00 | Providing and laying REINFORCED CEMENT CONCRETE OF M-25 GRADE with 20mm and down size graded crushed stone aggregates/gravel in SUB-STRUCTURE of all types e.g. foundations, footings, raft, beams, slabs, pile caps, retaining walls, jambs, counterforts, buttresses, trenches, manholes,pipe encasement, catchpits, drains, RCC pits, equipment/machine foundations, pedestals, pipe sleepers, columns, plinth beams, suspended floors, beams, staircases, landings, steps, brackets etc. (including single pour concreting upto 250m3), including cost of admixtures if used,providing pockets, openings, recesses, chamfering etc., wherever required, vibrating, tamping, curing and rendering if required to give a smooth and even surface etc. all complete (excluding the Cost of Reinforcement and Shuttering) for all depths below and upto plinth level in any shape, position and thickness etc. all complete as specified, shown and directed. | 85.00 | M3 |  | 15876.00 | 1592362.80 | 1592362.80 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
263.00 | Providing and laying REINFORCED CEMENT CONCRETE OF M-25 GRADE with 20mm and down size graded crushed stone aggregates/gravel in SUPER STRUCTURE in suspended floors, slabs, beams, columns, walls including counterforts, staircases, landings, steps, facias, fins, mouldings, gutters, shelves, windowsills, canopies, lintels, girders, ducts, brackets, chajjas with drip moulds, pedestals, posts, struts, equipment/machine foundations, ramps etc. (including single pour concreting upto 250m3) including cost of admixtures if used providing pockets, openings, recesses, chamfering wherever required, vibrating, tamping, curing and rendering if required to give a smooth and even surface etc. all complete (excluding the Cost of Reinforcement and Shuttering) for all heights above plinth level in any shape, position, thickness etc. all complete as specified, shown and directed. | 30.00 | M3 |  | 17346.00 | 614048.40 | 614048.40 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
264.00 | CENTERING AND SHUTTERING
265.00 | Providing and fixing CENTERING AND SHUTTERING in foundations, footings, raft beams, slabs, pile caps, retaining walls, jambs, counter-forts, buttresses, trenches, equipment/machine foundations, pedestals, abutments, pipe sleepers, columns, plinth beams, lintels, suspended slabs, beams, staircases, landings, steps, non-circular tunnels/bunkers/silos/ shafts/ hoppers/liquid storage structures etc. including shuttering for single pour concreting, strutting, bracing, propping etc., keeping the same in position during concreting and removal of the same after specified period etc. for Straight/ Inclined Shuttering, keeping necessary provision for inserts, projecting dowels, anchor bolts or any other fixture etc. all complete and as specified and directed. Plywood shall be good enough to keep finishing work.
266.00 | i) For all depths below and upto & inclusive of plinth level. | 100.00 | M2 |  | 735.00 | 86730.00 | 86730.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
267.00 | ii) For all heights above plinth level. | 80.00 | M2 |  | 882.00 | 83260.80 | 83260.80 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
268.00 | REINFORCEMENT
269.00 | Supplying and placing in position HIGH STRENGTH DEFORMED STEEL BARS REINFORCEMENT (conforming to IS:1786, Grade Fe 415), for R.C.C. work including transporting the Steel, straightening, cleaning, decoiling, cutting, bending to required shapes and lengths as per details, binding with contractor's own 16 SWG black soft annealed binding wire at every intersection, supplying and placing with proper cover blocks, supports, chairs, overlaps, welding, spacers, fanhooks etc. for all heights and depths etc. all complete as directed. | 6.50 | MT |  | 121.00 | 928.07 | 928.07 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
270.00 | STRUCTURAL STEEL WORKS
271.00 | Supplying, transporting, storing, fabricating in position and testing/examining bolted and/or welded STRUCTURAL STEEL WORKS at all levels and locations including all builtup sections/compound sections made out of rolled sections and/or plates/bent plates in trusses, purlins, wind ties, wind girders, columns, portals, racks, frameworks, crane gantries, surge girders, bracings, floor beams, lifting beams, monorails, platforms, staircases (excluding chequered plates and gratings), ladders, stoppers, brackets, side runners, sagrods, supports for pipe & equipment and technological accesories and process piping, hand railings, posts, conveyor galleries, trestles, towers, masts, junction houses etc., cutting to required size, straightening/bending if required, edge preparation, cleaning, preheating, bolting/welding of joints, (including sealing the joints of box sections with continuous welding), finishing edges by grinding, fixing in line and level with temporary staging & bracing and removal of the same after erection, grouting with Ordinary Grout or premix free flow Nonshrink Grout as specified, including preparation and submission of detailed fabrication drawings and applying primer after fabrication as per specification (for normal corrosive environment), etc. all complete | 3.00 | MT |  | 229320.00 | 811792.80 | 811792.80 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
272.00 | MISCELLANEOUS STEEL WORKS
273.00 | Supplying, fabricating, fixing and keeping in position at all levels and locations THREADED ANCHOR BOLTS of all diameters and nomenclature including nuts, washers, anchor plates, pipe sleeves etc. in foundations, columns, pedestals, slabs, beams, walls etc. or any other place as directed including handling & transporting, straightening if required, turning from relevant size M.S. rounds to required diameter, threading, welding, providing necessary templates and auxilliary dummy structures, if any, necessary tying and welding with reinforcement, adjustment of shuttering & reinforcement/any other fixture, greasing exposed metal surfaces, covering bolts and packing the sleeves with jute cloth etc. all complete as specified and directed. | 1.00 | MT |  | 203437.00 | 240055.66 | 240055.66 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
274.00 | Supplying, transporting, storing, fabricating and fixing in position M.S. METAL INSERT (with lugs) of any shape made out of flats, plates, rolled sections, pipes etc. providing necessary templates, staging, cutting, straightening, if required, bolting, welding as required and embedding in position on both Plain and Reinforced Cement concrete members inclusive of adjusting shuttering & reinforcement/any other fixture, welding where necessary, tying and holding to correct level, line and position, any auxilliary dummy structures to support the heavy inserts, painting exposed surfaces with a coat of Red Oxide Zinc Chromate Primer etc. all complete for all depths and heights as specified and directed. | 1.00 | MT |  | 164062.00 | 193593.16 | 193593.16 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
275.00 | Supplying, fabricating and erecting in position at all levels and locations bolted, clamped and/or welded GRATING (fabricated as per standards) made out of M.S. flats/M.S. flats with M.S. rounds in walkways, platforms, stair treads etc. including cutting to required size, shape, making holes, notches, openings of required size, nosing, straightening if required, making the edges smooth, removing the burrs, fabricating clamps, fixing, welding, preparation and submission of fabrication drawings and preparing the surfaces for painting, surface cleaning, wire brushing, removal of mill scale, dust, rust, oil or grease and applying one shop coat of Red Oxide Zinc Chromate Primer after fabrication etc. all complete as specified and directed. | 1.00 | MT |  | 236250.00 | 278775.00 | 278775.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
276.00 | BRICK MASONRY
277.00 | External Walls Ordinary plain cement plaster Average 18mm thick 1:4 (1 cement : 4 sand). Cement supplied by the Contractor at their cost. | 150.00 | M3 |  | 13814.00 | 2445078.00 | 2445078.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
278.00 | Painting of Walls External walls:- Providing & applying 3 coats of waterproof decorative cement paint of approved make and approved shade, cleaning, including preparation of surfaces,base primer, curing etc. all complete | 200.00 | M3 |  | 3996.00 | 943056.00 | 943056.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
279.00 | Supplying and filling of Bouldors
280.00 | Supplying and filling of various sizes and type of boulders as per site requirement or as per direction of EIC. Rate involves supply, transportation, unloading at site, laying, etc. to complete the work in all respect. | 10.00 | M3 |  | 3806.00 | 44910.80 | 44910.80 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
281.00 | SECTION-D [CATHODIC PROTECTION WORKS]
282.00 | CATHODIC PROTECTION SYSTEM
283.00 | All works shall be carried out as per approved drawings and specifications. Work shall include design / residual engineering, preparation of CP schematic drawing, supply, installation, testing and commissioning of complete CP system, all related civil work, including providing foundations, supply of all materials as specified in SCC, instruments, consumables, touch-up epoxy paint as required, including supply of paint, tools, tackles, labor, transportation for satisfactory completion of work and as per directions of EIC. In addition to the items mentioned below the Contractor's scope shall include connecting the new pipelines to existing pipelines/cathode-points of TR units by means of jumpering/bonding.
284.00 | Supply, laying & testing of 600 / 1100V grade single core, stranded tinned copper conductor cables, XLPE insulated / PVC sheathed, armoured as per IS of following sizes. The work shall include excavation for cable trenching at min. 1.2 m below GL in all types of soil including rock, backfilling of cable in trenches, lugging, ferrulling, making termination as per drawings & specification. Supply of all tools, tackles, consumables, etc. for completion of work, in all respect and as per directions of EIC.
285.00 | 25 mm2 | 30.00 | Mtr. |  | 1703.00 | 60286.20 | 60286.20 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
286.00 | 10 mm2 | 16.00 | Mtr. |  | 1703.00 | 32152.64 | 32152.64 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
287.00 | 6 mm2 | 30.00 | Mtr. |  | 1634.00 | 57843.60 | 57843.60 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
288.00 | Making cable to pipe connections
289.00 | Making cable to pipe connections by thermit welding for following cables, including excavation for exposing pipe, removal of coating / wrapping, thermit welding recoating of the area of weld by epoxy filling, holiday testing, backfilling, supply of all tool, tackles, consumables thermit weld kits & labour for satisfactory completion of work.
290.00 | 6 mm2 Cables | 2.00 | No. |  | 4262.00 | 10058.32 | 10058.32 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
291.00 | 10 mm2 Cables | 2.00 | No. |  | 4262.00 | 10058.32 | 10058.32 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
292.00 | 25 mm2 Cables | 2.00 | No. |  | 4524.00 | 10676.64 | 10676.64 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
293.00 | Supply & installation of Small test station as per enclosed drawings and technical specifications. Work shall include all related civil works including foundation, termination of cables inside the test stations along with lugs & ferules sealing of cable entry space with bitumen compound supply of all materials, consumables, tools, tackles, etc. for satisfactory completion of work and as per directions of EIC. | 3.00 | No. |  | 49218.00 | 174231.72 | 174231.72 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
294.00 | Supply, installation, testing and commissioning of spark-gap arrestors across insulating joints. | 3.00 | No. |  | 21758.00 | 77023.32 | 77023.32 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
295.00 | Supply and Installation of pipe to cable connection by Pin Brazing Encapsulation method | 12.00 | Nos. |  | 6427.00 | 91006.32 | 91006.32 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
296.00 | SECTION-E [ELECTRICAL WORKS]
297.00 | Supply, installation, testing, commissioning of Street Lighting Fixture suitable for 100 W LED Lamps with fixure with a well glass flamee proof design, Lighting Poles (4mtr Height) with aluminium paint complete with mounting bracket, flameproof control gear box, internal cable from fitting to junction box, flameproof fittings etc. including civil foundation with pipe inserts for cables and connecting work, with all material and labour as per specifications, drawings and instruction of EIC. Work to be completed in all respects. | 16.00 | Nos. |  | 62433.00 | 1178735.04 | 1178735.04 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
298.00 | Supply, installation, testing & commissioning of the complete earthing system, earth electrodes/pit, earth main ring, earthing of metering skid, electrical equipments, instrument panels, field instruments, process equipments & pipes / flanges including all associated civil work with all material & labour as per specification & drawings approved by the company. Each earthing system shall include the following.
299.00 | 65mm dia 3 Mtr. Long GI PIPE Electrode with 6mm thick chequered plate cover, display board etc | 8.00 | Nos. |  | 50760.00 | 479174.40 | 479174.40 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
300.00 | 600x600x3mm copper plate Electrode with 6 mm thick chequered plate cover, display board etc | 4.00 | Nos. |  | 85035.00 | 401365.20 | 401365.20 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
301.00 | GI Strip (50X6) mm | 200.00 | Mtrs. |  | 1095.00 | 258420.00 | 258420.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
302.00 | GI Strip (25X6) mm | 100.00 | Mtrs. |  | 786.00 | 92748.00 | 92748.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
303.00 | 1C 25 Sq.mm PVC insulated Cu Conductor (flexible type cable) | 130.00 | Mtrs. |  | 492.00 | 75472.80 | 75472.80 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
304.00 | 10 SWG GI wire | 300.00 | Mtrs. |  | 150.00 | 53100.00 | 53100.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
305.00 | GI Wire, Copper wire, wire rope and all balance earthing material including copper strip (50 mmX 2 mm thick) jumper for flanges etc. as per the specification. | 1.00 | Lot |  | 781987.00 | 922744.66 | 922744.66 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
306.00 | PVC Conduit including bend,tee, clamps, JB and other required assesories | 1.00 | LS |  | 689062.00 | 813093.16 | 813093.16 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
307.00 | Supply, laying, installation, termination, testing, commissioning of 1100 Volt PVC insulated, PVC sheathed and armoured / unarmoured cables in trenches, excavated underground / trays, pulling through pipes and its proper sealing including underground trench and supply of hume pipes for road crossing, etc. as required as per specifications and drawings approved by the company.
308.00 | 4C X 6 Sqmm Cu conductor XLPE Insulated Armoured Power Cable of 1100V Grade | 350.00 | Mtrs. |  | 624.00 | 257712.00 | 257712.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
309.00 | 3C X 2.5 Sqmm Cu conductor XLPE Insulated Armoured Power Cable of 1100V Grade | 100.00 | Mtrs. |  | 308.00 | 36344.00 | 36344.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
310.00 | Note: (1) The quantities given above against individual items are indicative and shall not be considered to be binding. The quantities may be increased, decreased or deleted at site at the time of actual execution. Procurement shall be done as per actual site condition, approved construction drawings and as per instruction of EIC. The unit rate shall be operated to work out the final payment to the contractor; (2) In each area, quantities given against individual item may be utilised / used for other consumers in same area.
311.00 | SECTION-F [INSTRUMENTATION WORKS]
312.00 | Supply, Calibration, Installation, testing and commissioning of instrumentation items listed below: (For details, refer instrumentation specifications)
313.00 | Pressure Gauge of different Range and rating as per site requirement Engineering , Design, Supply, testing, installation, erection and commissioning. Also supply of erection material like SS316 tube, SS316 fittings, manifold, mounting stand and all other required material. Bourdon type with 2-way manifold, direct mount, 150mm dial, wetted part SS316, IP 65 rated, blow out protection and shatter proof heavy duty glass. | 15.00 | Nos |  | 125009.00 | 2212659.30 | 2212659.30 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
314.00 | HARTconfigurator for above transmitters for configuration, re calibration and dignostic. | 1.00 | Nos |  | 1123500.00 | 1325730.00 | 1325730.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
315.00 | Pressure Gauge with Gauge Saver of different Range and rating as per site requirement Engineering , Design, Supply, testing, installation, erection and commissioning. Also supply of erection material like SS316 tube, SS316 fittings, manifold, mounting stand and all other required material. Bourdon type with 2-way manifold, direct mount, 150mm dial, wetted part SS316, IP 65 rated, Gauge Saver, blow out protection and shatter proof heavy duty glass. | 2.00 | Nos |  | 38023.00 | 89734.28 | 89734.28 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
316.00 | Pressure Transmitter of different Range and rating as per site requirement Engineering , Design, Supply, testing, installation, erection and commissioning. Also supply of erection material like SS316 tube, SS fittings, manifold, mounting stand and all other required material. Smart HART, Ex'd', IP-65, 24 VDC 2-wire loop powered. | 10.00 | Nos |  | 108609.00 | 1281586.20 | 1281586.20 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
317.00 | Temperature Transmitter of different Range and rating as per site requirement Engineering , Design, Supply, Installation, Calibration, Testing & Commissioning of Temperature Transmitters including mounting of Instrument on yoke, supply of yoke, supply and erection of supports for impulse lines wherever required, supply, fabrication & installation of SS manifolds/ SS impulse lines & SS valves & fittings with supports, testing and painting of supports. | 2.00 | Nos |  | 108609.00 | 256317.24 | 256317.24 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
318.00 | RTD Engineering , Design with wake frequency calculation, Supply , Installation, Calibration, Testing & Commissioning of RTD Flanged type thermowell (as per approved Piping GAD & Hookup drawings) inclusive of installation of thermowell on thepiping nozzle and installation of instruments as per General Specification-Instrumentation, Shall be skin type. | 2.00 | Nos |  | 112442.00 | 265363.12 | 265363.12 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
319.00 | Valve Junction Bob - Gas Over Oil Actauted Valve (GOOV) and or HOV of different size and rating as per site requirement Installation of valve junction box and their accessories inclusive of supply of necessary cable glands, terminals and complete with cabling, glanding, termination and earthing followed by testing and commissioning of complete gas over oil actuated valve. | 6.00 | Nos |  | 551250.00 | 3902850.00 | 3902850.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
320.00 | Instrumentation Local Control Panel as per the site requirement Engineering , Design, Supply, testing, installation, erection and commissioning of Wall Mounted CRCA Fully wired Wall Mounted Local Control Panel with all accessories including Signal distribution Card, Relays, Barriers, Digital Indicators, Power supply converter, MCBs, etc, complete in all respect as per the tender. The dimension of the local control panel shall be minimum 1200mm (H) x 800mm (W) x 450mm (D). Also, supply of all items required for erection , testing and commissioning is included in scope . Wall mounted compact panel with fully wired, indicators, lamps,status, RTU repetation etc | 2.00 | Sets |  | 590625.00 | 1393875.00 | 1393875.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
321.00 | Gas Detection System (GDS) - Channel cards only Supply, Configuration, testing, installation, erection and commissioning of channel card & field detectors suitable to existing LEL system in spare slots (Card OLDHAM) Model 6451424, MX-52 ). | 9.00 | Nos |  | 46921.00 | 498301.02 | 498301.02 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
322.00 | IR type, Flame proof, IP-65, housing material SS316 without display, range 0-100% LEL point hydrocarbon gas detector. | 9.00 | Nos |  | 164850.00 | 1750707.00 | 1750707.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
323.00 | Cables, Cables Trays and Junction boxes Supply, laying, installation, erection of signals cable from pressure transmitters, temperature transmitter to junction boxes, junction boxes to existing local control panel (LCP)/FC. including glanding, termination, ferruling, dressing etc. at both ends. Laying of cable from remote operated valve junction box to existing local control panel (LCP)/FC ncluding glanding, termination, ferruling, dressing etc. at both ends. Supply of cable trays, cables glands, junction boxes, erection materials, cable ferrules, cable lugs, cable tie. Installation and erection of cable trays and junction boxes Preparation of cable trench for burying cable, excavation, restoration of trench and compacting. Supply and laying of bricks and sand, pipes at all the crossings etc.
324.00 | 1P X 1 .5 Sq. mm Over all Screened | 350.00 | Mtr |  | 427.00 | 176351.00 | 176351.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
325.00 | 2P x 1.5 Sq. mm Over all Screened | 160.00 | Mtr |  | 572.00 | 107993.60 | 107993.60 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
326.00 | 4C x 1.5 Sq. mm Over all Screened | 160.00 | Mtr |  | 572.00 | 107993.60 | 107993.60 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
327.00 | 1Q X 1 .5 Sq. mm Over all Screened | 40.00 | Mtr |  | 754.00 | 35588.80 | 35588.80 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
328.00 | 12 P x 1.5 Sq. mm Individual and Over all Screened | 220.00 | Mtr |  | 1805.00 | 468578.00 | 468578.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
329.00 | 16 C x 1.5 Sq. mm Over all Screened | 660.00 | Mtr |  | 1372.00 | 1068513.60 | 1068513.60 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
330.00 | 1 T x 1.5 Sq. mm Over all Screened | 240.00 | Mtr |  | 625.00 | 177000.00 | 177000.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
331.00 | 8 T x 1.5 Sq. mm Individual and Over all Screened | 220.00 | Mtr |  | 1966.00 | 510373.60 | 510373.60 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
332.00 | 2C X 1 .5 Sq. mm Power cable | 80.00 | Mtr |  | 427.00 | 40308.80 | 40308.80 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
333.00 | 2C X 2 .5 Sq. mm Power cable | 80.00 | Mtr |  | 493.00 | 46539.20 | 46539.20 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
334.00 | Serial communication cable, Modbus RS - 485, PVC Sheathed, 4 pair | 100.00 | Mtr |  | 295.00 | 34810.00 | 34810.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
335.00 | Junction Box 'Flameproof Junction box as per specification with Plug and suitable for cable entries of single pair and multi pair cable as per the Instrument cable schedule | 6.00 | Nos |  | 75586.00 | 535148.88 | 535148.88 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
336.00 | Cable Trays (60 mm wide x 30 mm height) | 300.00 | Mtr |  | 951.00 | 336654.00 | 336654.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
337.00 | Cable Trays (100 mm wide x 30 mm height) | 100.00 | Mtr |  | 1148.00 | 135464.00 | 135464.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
338.00 | Cable Trays (300 mm wide x 30 mm height) | 150.00 | Mtr |  | 1292.00 | 228684.00 | 228684.00 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
339.00 | Multi cable Transit (MCT) block with stay plate and module as per the approved datasheet | 2.00 | Nos |  | 9843.00 | 23229.48 | 23229.48 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
340.00 | Canopy | 20.00 | Nos |  | 8531.00 | 201331.60 | 201331.60 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
341.00 | Pressure Reduction System (PRS) Testing & Commissioning assistance (For instrumentation part ) Laying of cables from skid JB to PRS/Metering panel and /or GC panel/TIC and metering panel and /or GC panel to RTU including glanding, termination, ferruling, dressing etc. at both ends and commissioning assistance. Installation and erection of cable trays, cable ferrules, cable lugs, cable tie, Making of cable trench, excavation, restoration of trench, supply and installation of bricks and sand, at all the crossings etc., arrangement of nitrogen cylinders (for skid testing). | 1.00 | No |  | 521718.00 | 615627.24 | 615627.24 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD
342.00 | Note: (1) The quantities given above against individual items are indicative and shall not be considered to be binding. The quantities may be increased, decreased or deleted at site at the time of actual execution. Procurement shall be done as per actual site condition, approved construction drawings and as per instruction of EIC. The unit rate shall be operated to work out the final payment to the contractor; (2) In each area, quantities given against individual item may be utilised / used for other consumers in same area.
| Total in Figures |  |  |  |  | 91432099.99
Lowest Amount Quoted BY: NARMADA OFFSHORE CONSTRUCTIONS PVT LTD(91432099.99)

## BOQ Summary
BOQ Summary Details Tender Title: COMPOSITE WORKS AT SV-18 MHASKAL AND NPL KALYAN Tender ID: 2026_GAIL_273651_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD (BID ID -1016104) | 91432099.99 | L1

## BoQDefects
Consolidated BoQ Defects Detail Tender Title: COMPOSITE WORKS AT SV-18 MHASKAL AND NPL KALYAN Tender ID: 2026_GAIL_273651_1
Sl.No | Bidder Name | BoQ Defects
1 | NARMADA OFFSHORE CONSTRUCTIONS PVT LTD | BoQ1-DT Mismatch-Cell-J115,BoQ1-DT Mismatch-Cell-J117,BoQ1-DT Mismatch-Cell-J119,BoQ1-DT Mismatch-Cell-J121,BoQ1-DT Mismatch-Cell-J122,BoQ1-DT Mismatch-Cell-J125,BoQ1-DT Mismatch-Cell-J128,BoQ1-DT Mismatch-Cell-J131,BoQ1-DT Mismatch-Cell-J135,BoQ1-DT Mismatch-Cell-J137,BoQ1-DT Mismatch-Cell-J139,BoQ1-DT Mismatch-Cell-J141,BoQ1-DT Mismatch-Cell-J143,BoQ1-DT Mismatch-Cell-J145,BoQ1-DT Mismatch-Cell-J147