## BoQ1
eProcurement System Government of India Created By: Gyanendra Singh Singh Vats Created Date/Time: 12-Oct-2026 11:50 AM Tender Title: Providing and fixing of Decorative street light pole along with other associated work in various places at IIT Delhi. Tender ID: 2026_IIT_926533_1
Tender Inviting Authority: Indian Institute of Technology Delhi
Name of Work : Providing and fixing of Decorative street light pole along with other associated work in various places at IIT Delhi.
Contract No: IITD/WORKS (SP- 5401) / 2026
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | B L ENTERPRISES (GSTN-09AHBPA2172K1ZK) BID ID -3484597 |  | Sangeeta Electricals (GSTN-NA) BID ID -3481749 |  | CHANDRA CONSTRUCTION (GSTN-NA) BID ID -3482164
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in existing surface/ recessed steel/ PVC conduit/ pole as required.
1.01 | 3 x 1.5 sq. mm | 300.00 | Metre | 100.00 | 132.00 | 39600.00 | 120.00 | 36000.00 | 185.00 | 55500.00 | 36000.00 | Sangeeta Electricals
2.00 | ﻿Supplying and making end termination with brass compression gland and aluminium lugs of following sizes of PVC insulated and PVC sheathed armoured aluminium conductor cable of 1.1 KV grade as required.
2.01 | 4 X 6 sq. mm (22 mm) | 174.00 | Each | 100.00 | 75.00 | 13050.00 | 50.00 | 8700.00 | 210.00 | 36540.00 | 8700.00 | Sangeeta Electricals
2.02 | 3½ X 25 sq. mm (28 mm) | 112.00 | Each | 100.00 | 124.00 | 13888.00 | 100.00 | 11200.00 | 415.00 | 46480.00 | 11200.00 | Sangeeta Electricals
2.03 | 3½ X 35 sq. mm (32 mm) | 6.00 | Each | 100.00 | 175.00 | 1050.00 | 150.00 | 900.00 | 550.00 | 3300.00 | 900.00 | Sangeeta Electricals
3.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
3.01 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 90.00 | Metre | 100.00 | 154.00 | 13860.00 | 130.00 | 11700.00 | 570.00 | 51300.00 | 11700.00 | Sangeeta Electricals
3.02 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 90.00 | Metre | 100.00 | 199.00 | 17910.00 | 180.00 | 16200.00 | 680.00 | 61200.00 | 16200.00 | Sangeeta Electricals
3.03 | 120 mm dia (OD-120 mm & ID-103 mm nominal) | 90.00 | Metre | 100.00 | 254.00 | 22860.00 | 230.00 | 20700.00 | 800.00 | 72000.00 | 20700.00 | Sangeeta Electricals
4.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 6.00 | Each | 100.00 | 3245.00 | 19470.00 | 3000.00 | 18000.00 | 8000.00 | 48000.00 | 18000.00 | Sangeeta Electricals
5.00 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | 50.00 | Metre | 100.00 | 28.00 | 1400.00 | 25.00 | 1250.00 | 150.00 | 7500.00 | 1250.00 | Sangeeta Electricals
6.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 100.00 | Metre | 100.00 | 30.00 | 3000.00 | 20.00 | 2000.00 | 130.00 | 13000.00 | 2000.00 | Sangeeta Electricals
7.00 | Supplying, Installation, Testing and Commissioning of LED based Spike light of dia 86mm and height 270mm including spike, housing made up of pressure die cast aluminum Alloy with effective thermal management, sturdiness and embossed brand name/logo name of manufacturer and optics made of surface mount reflector with toughened. The fixture should have a minimum system efficacy of 80 lumen/Watt and a minimum system lumen output of 700 lumens and maximum system wattage of 10 Watts.The fixture shall have a CRI of minimum 80 and beam angle: 50-55deg. The fixture shall be designed for a system life of 50,000 hours @70% lumen maintenance. Ingress Protection of IP65 (lamp and gear Compartment), CCT: 3000K. The fixture driver should have an operating voltage range of 150-270 V, surge protection of >=2.5KV, PF >0.9, THD<15% & Driver efficacy >85% @full load and rated voltage. Ambient temp range: 0deg to 45deg C. The Drivers should be a potted driver not a printed circuit board without casing, mounted inside the luminaire. The fixture should comply with the parameters as per IS10322. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. | 50.00 | Each | 100.00 | 3895.00 | 194750.00 | 3500.00 | 175000.00 | 2600.00 | 130000.00 | 130000.00 | CHANDRA CONSTRUCTION
8.00 | Supplying, Installation, Testing and Commissioning of 5 metre Decorative street light pole of cast iron Pole having Cast iron bottom around 625 mm. The Top Portion of the pole is made out of 90mm Galvanised tube Pole has a service window at bottom containing 25amp connector terminal and MCB of the desired rating. Complete Poles are primer coated and painted with polyurethane paint of the desired colour with Double arm ornamental brackets made out of Galvanised steel steel tubes with cast alum. embeliimenst and suitable for mounting of twin drop down hanging luminaires. The brackets are primer coated and painted with polyurethane paint and 2x60 Watts LED decorative hanging fixture with made out of spun alum with following specifications (top dia Ø450mm, height 450mm) of system efficacy 100lm/w with IP66, IK03 made out of aluminium housing. housing with PMMA lens with transparent diffuser. LED shall have CRI>70, L70: 50K hrs of burning, CCT: 5700/4000/3000K. Driver should have internal surge protection of 4KV and external surge protection of 10KV, iTHD<10%, driver efficiency>85% @full laod with complete CISPR15 compliance to avoid electromagnetic interference. Fixture should have ambient temperature of -10°C to +50°C. The Power LED’s are mounted on metal clad PCB’s then mounted on extruded / cast alum. Heat Sink and fitted with LED drivers. A UV stabilized PC/ PMMA clear/frosted diffuser is provided for Glare Free Lighting with high Visual comfort etc. complete as required. The fixture should comply with the parameters as per IS10322. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. complete as required. | 21.00 | Each | 100.00 | 69521.00 | 1459941.00 | 67500.00 | 1417500.00 | 58000.00 | 1218000.00 | 1218000.00 | CHANDRA CONSTRUCTION
9.00 | Supplying, Installation, Testing and Commissioning of 3 metre Decorative cast Iron Pole having Cast Iron bottom around 625 mm . The Top Portion of the pole is made out of 75mm Galvanised tube Pole has a service window at bottom containing 25amp connector terminal and MCB of the desired rating. Complete Poles are primer coated and painted with polyurethane paint of the desired colour with 40 Watts LED decorative Post top fixture with with minimum system lumens of 3900lm with IP66, IK10 body made of aluuminium body of top dia Ø366mm and height 370 mm with UV Protected PC diffuser for glare free lighting. LED should have CRI>70, CCT: 3000/4000K, L70:50K hrs of burning. LED driver should have PF>.95, THD<10%, driver efficiency >85%. Driver should have CISPR compliance to avoid electromagnetic interference. The Led's are mounted on metal clad PCB's and then LED's & PCB assembly are mounted on extruded aluminium Heat sink and fitted with Led Driver etc. complete as required. The fixture should comply with the parameters as per IS10322. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. | 30.00 | Each | 100.00 | 53290.00 | 1598700.00 | 48000.00 | 1440000.00 | 42000.00 | 1260000.00 | 1260000.00 | CHANDRA CONSTRUCTION
10.00 | Supplying, installation, testing and commissioning of 11Watts LED Decorative Bollard with System efficacy of 80 lm/W (880 lumens). Luminaire shall be made up of pure polyester power coated RAL7021 casted Aluminium housing with seamless polycarbonate diffuser, having dimension of dia(Ø) 140mm with height of 800mm. All external hardware must be of SS304 grade. LM 80-08 compliant LEDs of EMC/ceramic package from reputed makes such as Nichia/Cree/ Bridgelux/ Lumiled/ Osram/Seoul should be provided. LEDs used in the product shall comply with EN 62471 for Photo-biological safety and certificate for the same from manufacturer shall be provided. Luminaire shall be with IP65 and IK08 protection. The LED shall be compliant with LM80-08 standard with L70 life of 50000 Hrs tested at maximum current (Complete LM 80 test report for LED should be submitted for 10000 hrs of testing). The LEDs used should be with CCT of 4000/5700 K, CRI of Minimum 80 and SDCM <5. LEDs must be driven at max 70% of the rated current. MCPCB with Aluminium core and copper thickness of 35 micron to be used for LED mounting. LED Driver shall be silicone potted, Integrated type, Isolated, Constant Current with range 140-280V AC. Driver Efficiency > 80% & 3 KV internal surge protection, Power factor greater than 0.95 and total harmonic distortion (THD) of less than 10% should be integral to the luminaire. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Light fixture must have Dark Sky Certification to avoid light pollution and sky glow. Compliance to Indian Standards of IS10322 Part 5 / Sect 5:1967; 16105 : 2012; IS 16106 : 2012; IS 15885 (Part2/Sec13) : 2012; IS 16108 : 2012 should be there. | 35.00 | Nos. | 100.00 | 7321.00 | 256235.00 | 6000.00 | 210000.00 | 4600.00 | 161000.00 | 161000.00 | CHANDRA CONSTRUCTION
11.00 | Making RCC foundation of size 150 mm x 150 mm x 300mm with 1:1.5:3 (1cement,1.5coarse,3stone aggregate) complete with 10mm dia MS bar for reinforcement along with centering & shuttering , with excavation the soil & refilling, ramming, curring etc as required. | 50.00 | Each | 100.00 | 864.00 | 43200.00 | 750.00 | 37500.00 | 2400.00 | 120000.00 | 37500.00 | Sangeeta Electricals
12.00 | Making RCC foundation of size 250 mm x 250 mm x 600mm with 1:1.5:3 (1cement,1.5coarse,3stone aggregate) complete with 10mm dia MS bar for reinforcement along with centering & shuttering ,3/4 no. suitable dia G.I coated bolt and MS plate with double nuts, 85mm dia 45cm length flexible pvc pipe with excavation the soil & refilling, ramming, curring etc as required. | 35.00 | Each | 100.00 | 1340.00 | 46900.00 | 1000.00 | 35000.00 | 4800.00 | 168000.00 | 35000.00 | Sangeeta Electricals
13.00 | Making RCC foundation of size 450mm x 450mm x 1200mm with 1:1.5:3 (1cement,1.5coarse,3stone aggregate) complete with 10mm dia MS bar for reinforcement along with centering & shuttering ,4 no. 16 mm dia G.I coated bolt and MS plate with double nuts, 85mm dia 45cm length flexible pvc pipe with excavation the soil & refilling, ramming, curring etc as required. | 30.00 | Each | 100.00 | 3540.00 | 106200.00 | 3000.00 | 90000.00 | 6000.00 | 180000.00 | 90000.00 | Sangeeta Electricals
14.00 | Making RCC foundation of size 600mmx600mmx1300mm with 1:1.5:3 (1cement,1.5coarse,3stone aggregate) complete with 10mm dia MS bar for reinforcement along with centering & shuttering , 4 no. 16 mm dia G.I coated bolt with double nuts, 85mm dia 45cm length flexible pvc pipe with excavation the soil & refilling, ramming, curring etc as required. | 26.00 | Each | 100.00 | 4560.00 | 118560.00 | 4000.00 | 104000.00 | 7000.00 | 182000.00 | 104000.00 | Sangeeta Electricals
15.00 | Supplying and laying of following size PVC insulated, PVC sheathed XLPE aluminium conductor armored cable of Following size, 1.1 KV grade, direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc. as required.[conforming to I.S-1554/1/8].
15.01 | 3½ X 35 sq. mm | 100.00 | Metre | 100.00 | 643.00 | 64300.00 | 700.00 | 70000.00 | 390.00 | 39000.00 | 39000.00 | CHANDRA CONSTRUCTION
15.02 | 3½ X 25 sq. mm | 1200.00 | Metre | 100.00 | 523.00 | 627600.00 | 600.00 | 720000.00 | 320.00 | 384000.00 | 384000.00 | CHANDRA CONSTRUCTION
15.03 | 4 X 6 sq. mm | 400.00 | Metre | 100.00 | 442.00 | 176800.00 | 500.00 | 200000.00 | 150.00 | 60000.00 | 60000.00 | CHANDRA CONSTRUCTION
16.00 | Supplying and laying of following size PVC insulated, PVC sheathed XLPE aluminium conductor armored cable of Following size, 1.1 KV grade in the existing RCC/ HUME/ METAL pipe as required. [conforming to I.S-1554/1/8].
16.01 | 3½ X 35 sq. mm | 13.00 | Metre | 100.00 | 520.00 | 6760.00 | 650.00 | 8450.00 | 390.00 | 5070.00 | 5070.00 | CHANDRA CONSTRUCTION
16.02 | 3½ X 25 sq. mm | 116.00 | Metre | 100.00 | 463.00 | 53708.00 | 550.00 | 63800.00 | 320.00 | 37120.00 | 37120.00 | CHANDRA CONSTRUCTION
16.03 | 4 X 6 sq. mm | 50.00 | Metre | 100.00 | 398.00 | 19900.00 | 450.00 | 22500.00 | 170.00 | 8500.00 | 8500.00 | CHANDRA CONSTRUCTION
17.00 | Design, Fabrication, Supplying, testing & commissioning of Smart Panel with following feautres like Central control and monitoring, Energy and power quality monitoring, Configurable Time Schedules, Line fault detection and alerts, Real Time Alerts by SMS, email and app notifications, Web App and local control Fallback on manual mode, scalable and Secured communication etc. made up with front operated cubicle type Double Door, Front access free standing, dust and vermin proof (IP 65), Suitable for use at 415 volt, 3 phase, 4 wire, 50 Hertz made out of 2mm thick CRCA MS sheet with hinged, Gasketed (meta/ based neoprene) and lockable doors having structural reinforcement with suitable angle / channel / Tl Flat / sections including 3 mm thick gland plates with 2 nos. Earthing terminal and powder coated paint finish of approved shade over metal surface cleaned and treated with seven tank process complete with frame duly erection in ground and interconnection with copper conductor etc.as per below specifications :- Hybrid IoT Device ( GSM & RF) 5 Year warranty Incoming MCCB 4Pole 125 Amp - 1 Nos. Latch relay 3 No. 90 Amp. Outgoing MCB 1Pole 32/25 Amp - 9 Nos. 3 Phase Smart energy hybrid IoT device (GSM & RF) and 4P isolator for bypass arragement with RF and GSM Antenna subscription for online dasboard with the warranty of 05 years with RS485 communication protocol. | 3.00 | Each | 100.00 | 142100.00 | 426300.00 | 125000.00 | 375000.00 | 100000.00 | 300000.00 | 300000.00 | CHANDRA CONSTRUCTION
18.00 | Making the corecut out with boki of 100/ 150 mm dia inside the soil including making good the same etc. as required. | 50.00 | Metre | 100.00 | 639.00 | 31950.00 | 500.00 | 25000.00 | 200.00 | 10000.00 | 10000.00 | CHANDRA CONSTRUCTION
19.00 | Making the corecut out of 150 mm dia in RCC wall of 150mm thickness including making good the same etc. as required. | 50.00 | Each | 100.00 | 320.00 | 16000.00 | 400.00 | 20000.00 | 270.00 | 13500.00 | 13500.00 | CHANDRA CONSTRUCTION
20.00 | Dismantling of old Galvanised Mild steel Pole of size 5/ 6/ 7/ 8 metre with bracket etc.along with all accessories and depositing the same in the store/ safe place as directed by Engineer-in-Charge as complete as required. | 26.00 | Each | 100.00 | 1200.00 | 31200.00 | 500.00 | 13000.00 | 900.00 | 23400.00 | 13000.00 | Sangeeta Electricals
21.00 | Refixing of old Galvanised Mild steel Pole of size 5/ 6/ 7/ 8 metre with bracket etc.along with all accessories on existing foundation with complete connection as directed by Engineer-in-Charge as complete as required. | 26.00 | Each | 100.00 | 1600.00 | 41600.00 | 500.00 | 13000.00 | 1500.00 | 39000.00 | 13000.00 | Sangeeta Electricals
| Total in Figures |  |  |  |  | 5466692.00 |  | 5166400.00 |  | 4733410.00
Lowest Amount Quoted BY: CHANDRA CONSTRUCTION(4733410.00)

## BOQ Summary
BOQ Summary Details Tender Title: Providing and fixing of Decorative street light pole along with other associated work in various places at IIT Delhi. Tender ID: 2026_IIT_926533_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CHANDRA CONSTRUCTION (BID ID -3482164) | 4733410.00 | L1
| 2 | Sangeeta Electricals (BID ID -3481749) | 5166400.00 | L2
| 3 | B L ENTERPRISES (BID ID -3484597) | 5466692.00 | L3