## BoQ1
eProcurement System Government of India Created By: Rekha DVV Created Date/Time: 03-Oct-2026 03:20 PM Tender Title: Miscellaneous works for revamping of primary ventilation system for Press area, CFFP P Tender ID: 2026_NFC_926973_1
Tender Inviting Authority: NUCLEAR FUEL COMPLEX
Name of Work: Miscellaneous works for revamping of primary ventilation system for Press area, CFFP-P
Contract No: E/691/2026
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | RM CLEANROOM SOLUTIONS LLP (GSTN-NA) BID ID -3482188 |  | GRAVITY FILTRATION (GSTN-NA) BID ID -3482722 |  | MJ AIR SYSTEMS (GSTN-NA) BID ID -3485151
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Fabrication , supply and Installation of pulse jet filteration system of Air flow 10000 CMH ,Filter Area : > 200 m2; ACR : 65 m3/m2*hr ,RAV with 0.75 HP motor , Hemipleat filters , floor space :1800x1200 mm CDC Controller,Enclosure for Dust Bin, Control Panel Alarm integration with Broken bag detector & Level sensor . Refer Specifications sheet for MOC , filteration efficiency etc.(Vendors have to fill annexure A ) | 1.00 | Nos |  | 3115200.00 | 3115200.00 | 2950000.00 | 2950000.00 | 3245000.00 | 3245000.00 | 2950000.00 | GRAVITY FILTRATION
2.00 | Fabrication , supply , Installation and validation of Bag-In Bag-Out Housing as per the attached drawing Capacity : 8000 CFM MOC : SS304 No. of Stages : Single H13 HEPA Deep Pleat Box Type HEPA Filter Grade: H-13, Flow : High Flow Efficiency : 99.997% down to 0.3μm particle size, Media: Micro Glass Fiber, Separator : Aluminium foil MOC-Casing: Aluminium Extrusion Gasket: Neoprene Gasket on both side Temperature : 90 deg c IPD:350±10% Pa, FPD:750 Pa Unit size: 1490 H x 1520 Wx 695 D(2Hx2W) HEPA Filter size:610x610x292mm, 2000 CFM at 2.54 m/s, 04 Nos. | 2.00 | Nos |  | 1097400.00 | 2194800.00 | 1003000.00 | 2006000.00 | 1125000.00 | 2250000.00 | 2006000.00 | GRAVITY FILTRATION
3.00 | SS304 ducting with bends, reducers, dampers etc as per the attached drawing | 1.00 | Set |  | 885000.00 | 885000.00 | 973500.00 | 973500.00 | 950000.00 | 950000.00 | 885000.00 | RM CLEANROOM SOLUTIONS LLP
4.00 | Transportation, Installation & Commissioning | 1.00 | Set |  | 236000.00 | 236000.00 | 265500.00 | 265500.00 | 275000.00 | 275000.00 | 236000.00 | RM CLEANROOM SOLUTIONS LLP
5.00 | Fabrication , supply , Installation and validation of HEPA Unit as per the attached drawing for ID fan Capacity : 2000 CFM No. of Stages : Single H13 HEPA Locking : Double Cam Locking Deep Pleat Box Type HEPA Filter Grade: H-13, Flow : High Flow Efficiency : 99.997% down to 0.3μm particle size, Media: Micro Glass Fiber,Separator : Aluminium foil MOC-Casing: Aluminium Extrusion Gasket: Neoprene Gasket on inlet Temperature : 90 deg c IPD:350±10% Pa, FPD:750 Pa Unit size: 800 H x 745 Wx 1100 D HEPA Filter size:610x610x292mm, 2000 CFM at 2.54 m/s, 01 Nos. as per the attached drawing | 3.00 | Nos |  | 342200.00 | 1026600.00 | 354000.00 | 1062000.00 | 375000.00 | 1125000.00 | 1026600.00 | RM CLEANROOM SOLUTIONS LLP
| Total in Figures |  |  |  |  | 7457600.00 |  | 7257000.00 |  | 7845000.00
Lowest Amount Quoted BY: GRAVITY FILTRATION(7257000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Miscellaneous works for revamping of primary ventilation system for Press area, CFFP P Tender ID: 2026_NFC_926973_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | GRAVITY FILTRATION (BID ID -3482722) | 7257000.00 | L1
| 2 | RM CLEANROOM SOLUTIONS LLP (BID ID -3482188) | 7457600.00 | L2
| 3 | MJ AIR SYSTEMS (BID ID -3485151) | 7845000.00 | L3