## BoQ1
eProcurement System Government of India Created By: Leela Mangalore Created Date/Time: 15-Oct-2026 03:22 PM Tender Title: Providing Street Lights to Oil Jetty Area Tender ID: 2026_NMPT_924791_1
Tender Inviting Authority: Office of the Executive Engineer Electrical, New Mangalore Port Authority, Panambur, Mangalore, Karnataka - 575010
Name of Work: Providing Street Lights to Oil Jetty Area.
Contract No: 10/Street-Light/EE(E)II/1993/2026 Dated: 03/09/2026
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Bharath Electrical and instrumentation (GSTN-29AABPF4977E1ZN) BID ID -3476099 |  | M/s. Precision Electrical Works (GSTN-29AEJPR3412C1ZN) BID ID -3479750 |  | Raaj power solutions and facilities (GSTN-29AAWFR6162Q1ZX) BID ID -3481710 |  | RAY AL CONSOLIDATED CONSTRUCTION PRIVATE LIMITED (GSTN-NA) BID ID -3482165 |  | JK ELECTRICALS AND ENGINEERS (GSTN-NA) BID ID -3477769
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Fabrication, supplying and erection of 9 Mtrs long hot dip galvanized, Octagonal pole with BSEN 10025 GRADE S355JO steel plate for shaft, IS 2062 for base plate with door opening arrangements, including suitable boards, Bakelite sheet and MCB’s as per IS specifications suitable to withstand the wind speed of 47 m/s for 9 Mtr pole in single section and single joint welded as per IS 9595/IS10178AWS having dimensions bottom 155mm dia, top 70mm dia with 3mm thick suitable base plate 260x260x16mm, PCD 250 and suitable foundation bolts 4nos “J” type along with template and the pole shall be hot dip galvanised in single dipping with not less than 65micron as per ASTM-A123 and 153 etc. (excluding foundation) as per drawing appended. a) 9m-Top 70mm and Bottom 155mm dia (As per Technical Specifications) | 65.00 | Nos. | 12930.00 | 18200.00 | 1183000.00 | 13500.00 | 877500.00 | 11750.00 | 763750.00 | 13700.00 | 890500.00 | 15675.00 | 1018875.00 | 763750.00 | Raaj power solutions and facilities
2.00 | Supplying and fixing of Hot dip Galvanized M.S. Bracket suitable for outdoor Luminaries and mounted on octagonal pole using necessary bolts, nuts etc., complete. a) Single Arm Bracket with 1500mm Standard 40/50mm dia (As per Technical Specifications) | 60.00 | Nos. | 1210.00 | 2100.00 | 126000.00 | 1200.00 | 72000.00 | 1200.00 | 72000.00 | 1800.00 | 108000.00 | 1520.00 | 91200.00 | 72000.00 | M/s. Precision Electrical Works, Raaj power solutions and facilities
3.00 | Supply and fixing of hot dip Galvanized MS circular bracket of ID 750mm, fabricated with 40mm dia pipe, head frame & supports, mounting plates suitable for mounting 4 Nos. outdoor LED flood light luminaries on 9 mtr octagonal pole using necessary bolts, nuts etc. Complete. All the hardware shall be GI/stainless steel only. | 5.00 | Nos. | 1500.00 | 4500.00 | 22500.00 | 3250.00 | 16250.00 | 1500.00 | 7500.00 | 2000.00 | 10000.00 | 3325.00 | 16625.00 | 7500.00 | Raaj power solutions and facilities
4.00 | Supply & fixing of 200 Watts flame proof LED street light luminaries with die cast aluminium alloy housing and polycarbonate diffuser, inbuilt driver, lumens output not less than 20000 lumens system efficiency greater than 100 lumens/watt power factor > = 0.9, IP66 with 1 No. FLP gland | 30.00 | Nos. | 9890.00 | 18950.00 | 568500.00 | 10200.00 | 306000.00 | 10890.00 | 326700.00 | 14500.00 | 435000.00 | 16625.00 | 498750.00 | 306000.00 | M/s. Precision Electrical Works
5.00 | Supply & fixing of FLP junction box of size approx. 280mm x 280mm x 210mm with cable entries for looping from pole to pole and from JB to light fixture, 4 Nos. 16 Sqmm CBT connector, 1 no. 6 Amps DP MCB for light fixture control with suitable FLP cable glands, stoppers, clamps for fixing to the 9 Mrs. Octagonal pole etc. complete | 30.00 | Sets | 8880.00 | 9840.00 | 295200.00 | 6581.00 | 197430.00 | 7880.00 | 236400.00 | 8000.00 | 240000.00 | 6175.00 | 185250.00 | 185250.00 | JK ELECTRICALS AND ENGINEERS
6.00 | Supply & laying of 3C x 2.5 Sq.mm armoured FRLS copper cable from the JB to light fixture | 700.00 | Mtrs | 180.00 | 220.00 | 154000.00 | 165.00 | 115500.00 | 180.00 | 126000.00 | 240.00 | 168000.00 | 180.00 | 126000.00 | 115500.00 | M/s. Precision Electrical Works
7.00 | Supply of LED flood light luminaire - 200W with pressure die cast aluminium housing body for optimal thermal dissipation. Lamp compartment comprising of anti-glare clear diffuser with Injection moulded polycarbonate / clear glass material, delivering superior light output Rated life Burning Hrs 50000hr @ Lumen Maintenance of 70%, CCT > 5500K, IP 66 optical and electrical compartment & impact resistance of complete luminaire > IK08. Power Factor > 0.9 with mains, Surge Protection – M in 5KV along with Overvoltage / Overload, short circuit / miss-wiring protection. Compatible for pole mauling with outer dia of 40mm to 50mm.Universal Voltage driver to operate wide voltage range from 100V to 270V, 50/60 Hz application. Compliance to IS10322 / IEC60598, LM 79 & LM80 Adherence with RoHS. UL approved MCPCB. Top access street light with single screw to ensure ease of maintenance at the sight site location with minimized minimal tools.LED Light fixture with 200W System Power consumption. LED Efficiency > 130 1m/w, nominal CRI > 75. Luminaire manufacturer should have in- house facility accredited by NABL / CPRI & any Government certified agency & Design & Development facility certified by ISO9001 : 2008. Housing with supplier word mark / name shall be Engraved / Embossing on the die cast housing / Body part Warranty of 2 Years against any manufacturing defect working under standard electrical conditions as mentioned above should be given by LED manufacturer. | 20.00 | Nos. | 5376.00 | 7250.00 | 145000.00 | 4091.00 | 81820.00 | 5500.00 | 110000.00 | 7270.00 | 145400.00 | 4275.00 | 85500.00 | 81820.00 | M/s. Precision Electrical Works
8.00 | Supply of LED Streetlight luminaire-200W with pressure die cast aluminium housing body for optimal thermal dissipation. Lamp compartment comprising of anti-glare clear diffuser with Injection moulded polycarbonate material, delivering superior light output Rated life Burning Hrs 50000 hr @Lumen Maintenance of 70%, maximum light intensity should be between 60 degrees to 70 degrees. CCT >5500K, IP66 optical and electrical compartment & impact resistance of complete luminaire > IK08. Power Factor > 0.9 with mains, Surge Protection-Min 5KV along with Over voltage / Overload, short circuit / miss- wiring protection. Compatible for pole mounting with outer dia of 40mm to 50mm. Universal Voltage driver to operate wide voltage range from 100V to 270V 50 / 60Hz application. Compliance to IS10322/IEC60598, LM79&LM80 Adherence with RoHS. UL approved MCPCB. Top access street light with single screw to ensure ease of maintenance at the sight site location with minimized minimal tools.LED Light fixture with 200W System Power consumption. LED Efficiency > 1301m/w, nominal CRI > 75. Luminaire manufacturer should be accredited by NABL / CPRI & any Government certified agency & Design & Development facility certified by ISO 9001:2008. Housing with supplier word mark / name shall be Engraved / Embossing on the die cast housing / Body part. Warranty of 2 Years against any manufacturing defect working under standard electrical conditions as mentioned above should be given by LED manufacturer. | 30.00 | Nos. | 5477.00 | 8000.00 | 240000.00 | 4885.00 | 146550.00 | 5400.00 | 162000.00 | 6350.00 | 190500.00 | 4940.00 | 148200.00 | 146550.00 | M/s. Precision Electrical Works
9.00 | Providing foundation for 9 mtrs Octagonal pole including Earth Excavation and making of RCC foundation drawing using M 20 concrete, steel reinforcement, shuttering complete as per pole suppliers approved foundation drawing or depending upon site condition.(All supply materials included in this item) | 65.00 | Nos. | 4400.00 | 4600.00 | 299000.00 | 4500.00 | 292500.00 | 4400.00 | 286000.00 | 4400.00 | 286000.00 | 4750.00 | 308750.00 | 286000.00 | Raaj power solutions and facilities, RAY AL CONSOLIDATED CONSTRUCTION PRIVATE LIMITED
10.00 | Supply and drawing Flexible Multicore FRLS cable manufactured with electrolytic grade flexible copper with low conductor confirming to IS:8130-1984 and (virgin) PVC insulation sheathed suitable for working voltage up to 1100 volts as per IS-694:1990. a) 3C x 2.5 sq.mm | 330.00 | Mtrs | 90.00 | 130.00 | 42900.00 | 125.00 | 41250.00 | 95.00 | 31350.00 | 188.00 | 62040.00 | 133.00 | 43890.00 | 31350.00 | Raaj power solutions and facilities
11.00 | Supply of 1.1 KV LT Aluminium UG cable XLPE insulated. PVC extruded inner sheath armoured FRLS UG LT cable as per IS-7098 Part-1, Armouring strip thickness in average +5% and resistivity 14Ohms/Kms as per IS-3975. a) 4C x 16 sq.mm (As per Technical Specifications) | 2100.00 | Mtrs | 125.00 | 162.00 | 340200.00 | 153.00 | 321300.00 | 125.00 | 262500.00 | 204.00 | 428400.00 | 142.00 | 298200.00 | 262500.00 | Raaj power solutions and facilities
12.00 | Supply of 1.1 KV, XLPE insulated, PVC extruded inner sheath armoured FRLS UG LT cable as per IS-1554(Part-I) or IS-7098(Part-1), Armouring strip thickness and resistivity as per IS-3975. a) 3.5C x 50 sq.mm (As per Technical Specifications) | 500.00 | Mtrs | 264.00 | 390.00 | 195000.00 | 335.00 | 167500.00 | 275.00 | 137500.00 | 388.00 | 194000.00 | 323.00 | 161500.00 | 137500.00 | Raaj power solutions and facilities
13.00 | Labour charges for laying of 1.1 KV class XLPE LT UG cable in existing trench / GI pipe / stoneware pipe / on pole/ on concrete wall as required. a) 4C x 16 sq.mm | 2100.00 | Mtrs | 10.00 | 18.00 | 37800.00 | 10.00 | 21000.00 | 10.00 | 21000.00 | 30.00 | 63000.00 | 9.50 | 19950.00 | 19950.00 | JK ELECTRICALS AND ENGINEERS
14.00 | Labour charges for laying of 1.1 KV class XLPE LT UG cable in existing trench / GI pipe / stoneware pipe / on pole/ on concrete wall as required. a) 3.5C x 50 sq.mm | 500.00 | Mtrs | 15.00 | 30.00 | 15000.00 | 15.00 | 7500.00 | 15.00 | 7500.00 | 40.00 | 20000.00 | 19.00 | 9500.00 | 7500.00 | M/s. Precision Electrical Works, Raaj power solutions and facilities
15.00 | Earth work excavation for cable trench of 0.5 to 0.75 Mtr. Width and Depth upto 1 Mtr. Including trial pits, depositing on bank upto a lead of 50mtr. Supplying and Displaying necessary Danger boards and Lighting, refilling the trench to the required ground level and consolidating etc., complete. a) In Hard soil | 2600.00 | Mtrs | 180.00 | 120.00 | 312000.00 | 150.00 | 390000.00 | 175.00 | 455000.00 | 200.00 | 520000.00 | 142.00 | 369200.00 | 312000.00 | Bharath Electrical and instrumentation
16.00 | Supplying and laying Double walled corrugated DWC HDPE pipe as per IS 14930 part ll with necessary connecting sockets, couplings, Tees, bends, End caps of same materials in existing trench / duct / pole / on wall / on black stone wall with SS saddles / on poles / structure drawing the cable with supply and fixing DWC pipe with Aluminium clamps and stainless steel screws as required for drawing the cable as complete job. a) 63mm OD / 50mm ID | 2600.00 | Mtrs | 70.00 | 90.00 | 234000.00 | 50.00 | 130000.00 | 70.00 | 182000.00 | 400.00 | 1040000.00 | 85.00 | 221000.00 | 130000.00 | M/s. Precision Electrical Works
17.00 | Supplying and making end termination with double compressing glands, lugs of LT cable. a) 4C x 16 Sq.mm | 130.00 | Nos. | 1500.00 | 1200.00 | 156000.00 | 600.00 | 78000.00 | 500.00 | 65000.00 | 720.00 | 93600.00 | 380.00 | 49400.00 | 49400.00 | JK ELECTRICALS AND ENGINEERS
18.00 | Supplying and making end termination with glands, lugs of LT cable. a) 3.5C x 50 Sq.mm | 8.00 | Nos. | 500.00 | 1500.00 | 12000.00 | 500.00 | 4000.00 | 500.00 | 4000.00 | 950.00 | 7600.00 | 475.00 | 3800.00 | 3800.00 | JK ELECTRICALS AND ENGINEERS
19.00 | Supply and fixing of spiral Earth Electrodes as per standard technical specifications as per MESCOM. | 65.00 | Nos. | 100.00 | 200.00 | 13000.00 | 100.00 | 6500.00 | 150.00 | 9750.00 | 250.00 | 16250.00 | 104.00 | 6760.00 | 6500.00 | M/s. Precision Electrical Works
20.00 | Supplying and laying of 100mm dia B class GI pipes for culverts / drain crossing / GI pipe / trench and cable raising, work includes supplying collars, GI clamps and GI nuts, bolts, washers for fixing pipe to drain wall complete etc. | 60.00 | Mtrs | 150.00 | 2200.00 | 132000.00 | 500.00 | 30000.00 | 680.00 | 40800.00 | 1265.00 | 75900.00 | 157.00 | 9420.00 | 9420.00 | JK ELECTRICALS AND ENGINEERS
21.00 | Digging of trench for laying of LT cables and refill the trench, In some places concrete & asphalt whenever removed, refixed the paver blocks, reconcrete / asphalt the road in hard soil, 1.5m deep x 0.5m wide (concrete cutting). | 60.00 | Mtrs | 650.00 | 750.00 | 45000.00 | 600.00 | 36000.00 | 550.00 | 33000.00 | 900.00 | 54000.00 | 665.00 | 39900.00 | 33000.00 | Raaj power solutions and facilities
22.00 | Providing / stone masonry foundation for control panel and the dimension of the foundation 800(W)x1000(H)x400(D) mm and the gap between the pillars is 350mm for cable connection to the control panel. The foundation starts 300mmbelow the ground after making 100 mm stone soling and curing etc. The panel should be stand on the 4 stainless steel bolts (12mmx6”) each bolt with four nuts & washers at 50mm height from the foundation and complete. | 4.00 | Nos. | 3500.00 | 3200.00 | 12800.00 | 3500.00 | 14000.00 | 3500.00 | 14000.00 | 4500.00 | 18000.00 | 3562.00 | 14248.00 | 12800.00 | Bharath Electrical and instrumentation
23.00 | Supply of SS 304 grade stainless steel (IP-54) enclosure of size 600(W)x760(H)x210(D)mm with rain canopy single door type with cam lock door sealing gasket and gland plate with required openings etc. Material 2mm thick and mounting plate 2.5mm thick comprising the following components with control wiring 10sq.mm copper wire for lighting circuit. Work including supply and fixing of the components 1 No. 125 Amps MCCB 4 pole 35KA as Incomer and 3 Nos 63 Amps MCCB for out goings, 50amps CBT connectors 16 Nos. 1 no. MNX 50amps contactor 3 pole with 1 no. timer 24 hours & 1 no. Auto manual selector to bypass the contactor. | 4.00 | Nos. | 60000.00 | 80000.00 | 320000.00 | 65000.00 | 260000.00 | 70000.00 | 280000.00 | 161460.00 | 645840.00 | 47500.00 | 190000.00 | 190000.00 | JK ELECTRICALS AND ENGINEERS
24.00 | Charges for trimming of tree branches wherever street light poles erected under the tree | 1.00 | Job | 3500.00 | 5000.00 | 5000.00 | 3500.00 | 3500.00 | 3500.00 | 3500.00 | 3200.00 | 3200.00 | 4750.00 | 4750.00 | 3200.00 | RAY AL CONSOLIDATED CONSTRUCTION PRIVATE LIMITED
25.00 | Supplying, fixing and wiring earth electrode for panel using 40 mm dia, 2.90 mm thick GI pipe 2.5 Mtr long with funnel with mesh and suitable size reducer fixed on the top of the Electrode. The funnel should be enclosed in a CC chamber of 400x400x400 mm with cast iron cover. The electrode shall have staggered holes of 12mm dia and the electrode covered 150 mm all-round with alternate layers of salt and char coal from the bottom of the CC chamber. The connection from the electrode is to be established through GI strip using GI bolts and nuts. | 4.00 | Nos. | 4500.00 | 12500.00 | 50000.00 | 4500.00 | 18000.00 | 5000.00 | 20000.00 | 5175.00 | 20700.00 | 6175.00 | 24700.00 | 18000.00 | M/s. Precision Electrical Works
26.00 | Supplying and running GI strip for grounding connections, using necessary fixing materials as required. a) 25 x 6 mm GI strip | 36.00 | Mtrs | 140.00 | 190.00 | 6840.00 | 140.00 | 5040.00 | 225.00 | 8100.00 | 125.00 | 4500.00 | 190.00 | 6840.00 | 4500.00 | RAY AL CONSOLIDATED CONSTRUCTION PRIVATE LIMITED
27.00 | Releasing and shifting of MESCOM RCC poles from site to ESD IV | 10.00 | Nos. | 400.00 | 3500.00 | 35000.00 | 400.00 | 4000.00 | 400.00 | 4000.00 | 400.00 | 4000.00 | 475.00 | 4750.00 | 4000.00 | M/s. Precision Electrical Works, Raaj power solutions and facilities, RAY AL CONSOLIDATED CONSTRUCTION PRIVATE LIMITED
28.00 | Supplying and installing cable route marker made up of RCC Block of size 100cm (H) x 50cm (W) x 6cm (D) indicating Embossed text as “NMP LT Cable“ with yellow paint a red colour letters and fixing with cement concrete. | 15.00 | Nos. | 650.00 | 1200.00 | 18000.00 | 650.00 | 9750.00 | 650.00 | 9750.00 | 650.00 | 9750.00 | 475.00 | 7125.00 | 7125.00 | JK ELECTRICALS AND ENGINEERS
| Total in Figures |  |  |  |  | 5015740.00 |  | 3652890.00 |  | 3679100.00 |  | 5754180.00 |  | 3964083.00
Lowest Amount Quoted BY: M/s. Precision Electrical Works(3652890.00)

## BOQ Summary
BOQ Summary Details Tender Title: Providing Street Lights to Oil Jetty Area Tender ID: 2026_NMPT_924791_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s. Precision Electrical Works (BID ID -3479750) | 3652890.00 | L1
| 2 | Raaj power solutions and facilities (BID ID -3481710) | 3679100.00 | L2
| 3 | JK ELECTRICALS AND ENGINEERS (BID ID -3477769) | 3964083.00 | L3
| 4 | Bharath Electrical and instrumentation (BID ID -3476099) | 5015740.00 | L4
| 5 | RAY AL CONSOLIDATED CONSTRUCTION PRIVATE LIMITED (BID ID -3482165) | 5754180.00 | L5