## BoQ1
Government eProcurement System Created By: Manoj Kumar Singh Created Date/Time: 15-Jun-2026 01:05 PM Tender Title: Supply, fabrication, installation of ventilation, fire fighting and Tender ID: 2026_NPCIL_267208_1
Tender Inviting Authority: In Charge, CMM (Works)
Name of Work: Supply, fabrication, installation of ventilation, fire fighting and chilled water systems of UKZ & UBZ tunnels of KKNPP-5
Tender No: NPCIL/KK-5&6/CONST/MECH/PT/2026/15
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Som Projects Pvt. Ltd. (GSTN-NA) BID ID -994255 |  | Agnice Fire Protection Private Limited (GSTN-NA) BID ID -993000 |  | TAP TURBO ENGINEERS PRIVATE LIMITED (GSTN-NA) BID ID -988768 |  | WELTECH ENGINEERS (GSTN-NA) BID ID -990032 |  | MGR FABRICATORS PRIVATE LIMITED (GSTN-NA) BID ID -990411
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply fabrication and Erection of Carbon Steel (CS) Ducting: The work involves a)Supply of cold rolled Carbon Steel sheets of thickness 2.00 mm as confirming to IS 513-2008 of designation CR3. b)preparation of circular/rectangular section duct/ fittings fabrication, development & cutting plan/ drawings for Engineer’s acceptance, rolling, cutting of sheets to required size & shape, bending, edge preparation, drilling, weld fit up, TIG welding for fabrication of circular and rectangular ducts & fittings such as bends, elbows, taps, T-joints, reducers fitted with vanes/ splitters of various sizes, collar piece for grill and mesh fixing, access doors in the duct as per WD and technical specifications c)erection of circular/rectangular section ducts & fittings at site, welding using GTAW process, mounting on permanent supports as shown in working drawings. performing non destructive testing such as DPT, root & final dye penetrant testing of weld joint, deploying NDT qualified personnel in ISNT/ ASNT level-2 and post cleaning of weld joint, visual inspection. d)Preparation of erection reports, as built drawing, CCC required for completion of work as per the technical specifications and drawing. This work also includes arrangement of all tools and tackles, machineries, consumables, welding filler wire, manpower of all categaries required for execution of work. | 2091.00 | Sq-m | 100.00 | 8700.00 | 18191700.00 | 8716.00 | 18225156.00 | 8175.00 | 17093925.00 | 6890.00 | 14406990.00 | 8750.00 | 18296250.00 | 14406990.00 | WELTECH ENGINEERS
2.00 | Instrumentation hole (ih) points in CS duct: Supply and erection of instrumentation hole setup (ih) points over CS ducts as per the specifications The work also involves, driling of hole in duct, welding, fixing of bolt, touchup painting as per WD and specifications. | 15.00 | nos | 10.00 | 550.00 | 8250.00 | 18649.00 | 279735.00 | 3400.00 | 51000.00 | 563.00 | 8445.00 | 700.00 | 10500.00 | 8250.00 | Som Projects Pvt. Ltd.
3.00 | Supply and application of Paint in Carbon Steel Ducting: The work includes Supply of paint and zinc rich epoxy primer and Surface preparation, grit blasting, application of approved painting system consisting of zinc rich epoxy primer, finish epoxy painting of approved shade as per technical specification on both side surfaces of ducts, duct fittings, vanes. | 4182.00 | Sqm | 100.00 | 3000.00 | 12546000.00 | 2496.00 | 10438272.00 | 885.00 | 3701070.00 | 2975.00 | 12441450.00 | 1800.00 | 7527600.00 | 3701070.00 | TAP TURBO ENGINEERS PRIVATE LIMITED
4.00 | Supply, fabrication and Erection of GI Ducting and fittings: Supply of various thickness Galvanized steel sheets confirming to IS: 277-2008, designation GPD, grade of zinc coating 275 for 0.7 mm (base material as per IS 513 designation. CR3), transportation, preparation and submission of Incoming material inspection report (IMIR), storage, preparation of duct/ fitting fabrication drawings for engineer’s acceptance, cutting of sheets to required size & shape, bending, rolling, edge preparation pitts burg lock seam/ grooved seam, spiral seam for circular ducts and rectangular ducts & fittings such as bends, elbows, taps, T-joints, reducers of various sizes, collar piece, exhaust hoods, access doors, erection of ducts & fittings at site with metal flanged connection, mounting on permanent supports at various elevations as per technical specifications and drawings. This work also includes supply and joining by GI rivets, fasteners, nut-washers as per IS 1363 & IS 1367 of property class 5.6, 5 mm thick EPDM/ Neoprene self adhesive gasket of equal flange width for flange connection, supply and application of silicon duct sealant, inspection as per specification and drawings, providing tools & tackles, machineries, manpower, preparation and handing over of as built drawings, reports, construction completion certificate (CCC) for following items.
5.00 | GI duct and fittings 0.7 mm Circular and rectangular | 2831.00 | SqM | 10.00 | 2320.00 | 6567920.00 | 5906.00 | 16719886.00 | 2370.00 | 6709470.00 | 2025.00 | 5732775.00 | 3500.00 | 9908500.00 | 5732775.00 | WELTECH ENGINEERS
6.00 | Supply and erection of ih.(inspection hole) arrangement as per for GI duct: This work also involves marking, drilling of required opening in the GI duct, cleaning and erection of i.h setup in duct as per technical specification | 25.00 | nos | 100.00 | 550.00 | 13750.00 | 18649.00 | 466225.00 | 3400.00 | 85000.00 | 540.00 | 13500.00 | 700.00 | 17500.00 | 13500.00 | WELTECH ENGINEERS
7.00 | Supply and Erection of Metal Mesh over Carbon Steel (CS & GI) Ducting: Supply, fabrication and erection of metal wire mesh size 10 mm x 10 mm and wire dia 1 mm over ventilation ducting as per the drawings and technical specifications. This work also includes cutting and making opening in the air duct by cutting/ grinding wheel, welding of fabricated metal mesh over the duct as per the specification, arrangement of tools & tackles, machineries, consumables, welding filler wire, manpower required for execution of work. | 46.00 | Sq-m | 10.00 | 4500.00 | 207000.00 | 6233.00 | 286718.00 | 1005.00 | 46230.00 | 5664.00 | 260544.00 | 3500.00 | 161000.00 | 46230.00 | TAP TURBO ENGINEERS PRIVATE LIMITED
8.00 | Supply, fabrication and Erection of Structural Steel: Supply of structural steel material conforming to IS 2062, E250, Quality BR consisting plates/ sheets/ angle/ channel/ beam and various profile as per IS 808, metal gratings, fasteners as per IS 1363 grade 5.6 and grade 8.8 etc, transportation, storage, handling, fabrication of ventilation duct support structure, fitup & welding, shifting, erection, site welding, inspection as per drawing and technical specification. This work also includes providing scaffolding / temporary platforms, man power, tools, tackles, plant and machineries, welding electrodes, other consumables and preparation of reports and submission for accpetance. | 15797.00 | kg | 100.00 | 300.00 | 4739100.00 | 313.00 | 4944461.00 | 260.00 | 4107220.00 | 242.00 | 3822874.00 | 285.00 | 4502145.00 | 3822874.00 | WELTECH ENGINEERS
9.00 | Grit blasting and supply and application of primer for support structures : Handling of supports, metal structure, shifting to blasting area, grit blasting using steel grits/shot,supply & application of Inorganic Zinc Silicate primer with minimum thickness(DFT) of 75 microns as per technical specification , inspection, testing, preparation of reports and work completion as per drawings, documents and specifications. The scope includes assesement of material requirement, procurement of grit/shot, primer with material test certificate, inspection at contractor's store, preparation of IMIR (incoming material inspection report) arrangement of expert man power, tools & tackles, P&M, consumables, cleaning aids etc with acceptance of EIC. Note : Work includes application of primer on field weld joints for metal structures after welding. | 16587.00 | kg | 100.00 | 50.00 | 829350.00 | 203.00 | 3367161.00 | 40.00 | 663480.00 | 76.00 | 1260612.00 | 30.00 | 497610.00 | 497610.00 | MGR FABRICATORS PRIVATE LIMITED
10.00 | Supply & Application of finish paint coats on structure: Identification of metal structures, surface cleaning, supply and application of finish paint of two coats of High build epozy painting of thickness 80-90 microns each on outside surface of specified color shade, inspection, preparation of reports, testing and work completion as per the drawings, documents and specification with acceptance of EIC. The work scope includes assessment of material requirement, procurement with material test certificate, handling, inspection at contractor's store, establishment of workshop, application, arrangement of man power, qualification of procedures, scaffolding and platforms, tools & tackles, P&M, consumables Note : Work includes application of paint on field weld joints for metal structures after welding. | 16587.00 | Kg | 10.00 | 28.00 | 464436.00 | 236.00 | 3914532.00 | 30.00 | 497610.00 | 41.00 | 680067.00 | 17.00 | 281979.00 | 281979.00 | MGR FABRICATORS PRIVATE LIMITED
11.00 | Supply of various sizes of Hilti Anchor fasteners & Fixing of hilti anchor fasteners using hammer drilling method: The work involves supply of various sizes of Hilti Anchor fasteners and hole drilling in the wall, cleaning and fixing of Hilti anchor fasteners using hammer drilling method in various buildings, location & positions as per the developed drawings and specification. This work includes providing manpower,identification, marking, providing hilti machine of required capacities, shifting & positioning, tools, tackles, performing drilling using drill bit in reinforced concrete by qualified operators, cleaning, torqueing with torque wrenches, cleaning aids, preparation of reports and submission for acceptance.
12.00 | HSL4-G M10 of all types | 610.00 | nos | 10.00 | 1150.00 | 701500.00 | 2029.00 | 1237690.00 | 1745.00 | 1064450.00 | 1050.00 | 640500.00 | 1470.00 | 896700.00 | 640500.00 | WELTECH ENGINEERS
13.00 | HSL4-G M12 of all types | 850.00 | nos | 10.00 | 1500.00 | 1275000.00 | 2265.00 | 1925250.00 | 2695.00 | 2290750.00 | 1890.00 | 1606500.00 | 1680.00 | 1428000.00 | 1275000.00 | Som Projects Pvt. Ltd.
14.00 | Supply of carbon steel pipes. The work includes supply of Carbon steel pipes conforming to ASME B36.10 ASME SA-106 Gr.B
15.00 | Pipe 150 NB Schdule 40 | 804.00 | Meter | 10.00 | 3650.00 | 2934600.00 | 4119.00 | 3311676.00 | 5765.00 | 4635060.00 | 3520.00 | 2830080.00 | 3925.00 | 3155700.00 | 2830080.00 | WELTECH ENGINEERS
16.00 | Pipe 125 NB Schdule 40 | 4548.00 | Meter | 10.00 | 2880.00 | 13098240.00 | 3227.00 | 14676396.00 | 4075.00 | 18533100.00 | 2384.00 | 10842432.00 | 3400.00 | 15463200.00 | 10842432.00 | WELTECH ENGINEERS
17.00 | Pipe 100 NB Schdule 40 | 2610.00 | Meter | 10.00 | 2150.00 | 5611500.00 | 2383.00 | 6219630.00 | 3220.00 | 8404200.00 | 1930.00 | 5037300.00 | 2325.00 | 6068250.00 | 5037300.00 | WELTECH ENGINEERS
18.00 | Pipe 80 NB Schdule 40 | 3804.00 | Meter | 10.00 | 1520.00 | 5782080.00 | 1675.00 | 6371700.00 | 2235.00 | 8501940.00 | 1488.00 | 5660352.00 | 1680.00 | 6390720.00 | 5660352.00 | WELTECH ENGINEERS
19.00 | Pipe 50 NB Schdule 40 | 684.00 | Meter | 10.00 | 780.00 | 533520.00 | 808.00 | 552672.00 | 1176.00 | 804384.00 | 710.00 | 485640.00 | 760.00 | 519840.00 | 485640.00 | WELTECH ENGINEERS
20.00 | Pipe 25 NB Schdule 40 | 792.00 | Meter | 10.00 | 550.00 | 435600.00 | 521.00 | 412632.00 | 605.00 | 479160.00 | 561.00 | 444312.00 | 525.00 | 415800.00 | 412632.00 | Agnice Fire Protection Private Limited
21.00 | Supply of carbon steel pipe fittings The work includes supply of Carbon steel pipes fittings conforming to ASME B 16.9 ASME SA-234 Gr.WPB for wrought fittings and ASME B 16.11 ASME SA-105 for forged fittings
22.00 | Bend90 150 NB Schdule 40 | 32.00 | Nos | 10.00 | 2250.00 | 72000.00 | 3502.00 | 112064.00 | 5220.00 | 167040.00 | 1955.00 | 62560.00 | 2950.00 | 94400.00 | 62560.00 | WELTECH ENGINEERS
23.00 | Bend45 150 NB Schdule 40 | 28.00 | Nos | 10.00 | 1200.00 | 33600.00 | 2501.00 | 70028.00 | 3650.00 | 102200.00 | 1105.00 | 30940.00 | 1750.00 | 49000.00 | 30940.00 | WELTECH ENGINEERS
24.00 | Bend90 125 NB Schdule 40 | 145.00 | Nos | 10.00 | 1450.00 | 210250.00 | 2331.00 | 337995.00 | 3980.00 | 577100.00 | 1360.00 | 197200.00 | 1750.00 | 253750.00 | 197200.00 | WELTECH ENGINEERS
25.00 | Bend45 125 NB Schdule 40 | 168.00 | Nos | 10.00 | 840.00 | 141120.00 | 1680.00 | 282240.00 | 2910.00 | 488880.00 | 722.00 | 121296.00 | 1125.00 | 189000.00 | 121296.00 | WELTECH ENGINEERS
26.00 | Bend90 100 NB Schdule 40 | 112.00 | Nos | 10.00 | 980.00 | 109760.00 | 1457.00 | 163184.00 | 2495.00 | 279440.00 | 893.00 | 100016.00 | 1250.00 | 140000.00 | 100016.00 | WELTECH ENGINEERS
27.00 | Bend45 100 NB Schdule 40 | 106.00 | Nos | 10.00 | 580.00 | 61480.00 | 1070.00 | 113420.00 | 1836.00 | 194616.00 | 467.00 | 49502.00 | 800.00 | 84800.00 | 49502.00 | WELTECH ENGINEERS
28.00 | Bend90 80 NB Schdule 40 | 107.00 | Nos | 10.00 | 520.00 | 55640.00 | 921.00 | 98547.00 | 1340.00 | 143380.00 | 459.00 | 49113.00 | 725.00 | 77575.00 | 49113.00 | WELTECH ENGINEERS
29.00 | Bend45 80 NB Schdule 40 | 109.00 | Nos | 10.00 | 360.00 | 39240.00 | 697.00 | 75973.00 | 1011.00 | 110199.00 | 315.00 | 34335.00 | 450.00 | 49050.00 | 34335.00 | WELTECH ENGINEERS
30.00 | Bend90 50 NB Schdule 40 | 57.00 | Nos | 10.00 | 260.00 | 14820.00 | 404.00 | 23028.00 | 925.00 | 52725.00 | 238.00 | 13566.00 | 300.00 | 17100.00 | 13566.00 | WELTECH ENGINEERS
31.00 | Bend45 50 NB Schdule 40 | 28.00 | Nos | 10.00 | 180.00 | 5040.00 | 333.00 | 9324.00 | 680.00 | 19040.00 | 162.00 | 4536.00 | 200.00 | 5600.00 | 4536.00 | WELTECH ENGINEERS
32.00 | Bend90 25 NB Schdule 40 | 2282.00 | Nos | 10.00 | 90.00 | 205380.00 | 271.00 | 618422.00 | 430.00 | 981260.00 | 85.00 | 193970.00 | 300.00 | 684600.00 | 193970.00 | WELTECH ENGINEERS
33.00 | Tee 125 NB Schdule 40 | 8.00 | Nos | 10.00 | 1880.00 | 15040.00 | 3191.00 | 25528.00 | 4810.00 | 38480.00 | 1700.00 | 13600.00 | 3350.00 | 26800.00 | 13600.00 | WELTECH ENGINEERS
34.00 | Tee 125NB-100NB Schedule 40 | 4.00 | Nos | 10.00 | 2040.00 | 8160.00 | 3191.00 | 12764.00 | 4810.00 | 19240.00 | 1762.00 | 7048.00 | 3350.00 | 13400.00 | 7048.00 | WELTECH ENGINEERS
35.00 | Tee 125 NB -80 NB Schdule 40 | 425.00 | Nos | 10.00 | 1910.00 | 811750.00 | 3191.00 | 1356175.00 | 4811.00 | 2044675.00 | 1615.00 | 686375.00 | 3300.00 | 1402500.00 | 686375.00 | WELTECH ENGINEERS
36.00 | Tee 100 NB Schdule 40 | 8.00 | Nos | 10.00 | 1290.00 | 10320.00 | 2040.00 | 16320.00 | 3650.00 | 29200.00 | 1190.00 | 9520.00 | 2200.00 | 17600.00 | 9520.00 | WELTECH ENGINEERS
37.00 | Tee 100 NB-80 NB Schdule 40 | 360.00 | Nos | 10.00 | 1140.00 | 410400.00 | 2040.00 | 734400.00 | 3650.00 | 1314000.00 | 850.00 | 306000.00 | 2200.00 | 792000.00 | 306000.00 | WELTECH ENGINEERS
38.00 | Tee 80 NB Schdule 40 | 25.00 | Nos | 10.00 | 850.00 | 21250.00 | 1362.00 | 34050.00 | 2165.00 | 54125.00 | 722.00 | 18050.00 | 1350.00 | 33750.00 | 18050.00 | WELTECH ENGINEERS
39.00 | Tee 80 NB -50 NB Schdule 40 | 160.00 | Nos | 10.00 | 720.00 | 115200.00 | 1362.00 | 217920.00 | 2165.00 | 346400.00 | 638.00 | 102080.00 | 1350.00 | 216000.00 | 102080.00 | WELTECH ENGINEERS
40.00 | Tee 50 NB-25 NB Schdule 40 | 171.00 | Nos | 10.00 | 410.00 | 70110.00 | 641.00 | 109611.00 | 1090.00 | 186390.00 | 357.00 | 61047.00 | 675.00 | 115425.00 | 61047.00 | WELTECH ENGINEERS
41.00 | Tee 50 NB Schdule 40 | 4.00 | Nos | 10.00 | 410.00 | 1640.00 | 641.00 | 2564.00 | 1090.00 | 4360.00 | 366.00 | 1464.00 | 675.00 | 2700.00 | 1464.00 | WELTECH ENGINEERS
42.00 | E Reducer 125 NB -100 NB Schdule 40 | 15.00 | Nos | 10.00 | 750.00 | 11250.00 | 1210.00 | 18150.00 | 2495.00 | 37425.00 | 680.00 | 10200.00 | 850.00 | 12750.00 | 10200.00 | WELTECH ENGINEERS
43.00 | E Reducer 125 NB -80 NB Schdule 40 | 3.00 | Nos | 10.00 | 660.00 | 1980.00 | 1265.00 | 3795.00 | 2495.00 | 7485.00 | 468.00 | 1404.00 | 950.00 | 2850.00 | 1404.00 | WELTECH ENGINEERS
44.00 | E Reducer 100 NB -80 NB Schdule 40 | 36.00 | Nos | 10.00 | 440.00 | 15840.00 | 775.00 | 27900.00 | 2080.00 | 74880.00 | 382.00 | 13752.00 | 550.00 | 19800.00 | 13752.00 | WELTECH ENGINEERS
45.00 | E Reducer 80 NB -50 NB Schdule 40 | 64.00 | Nos | 10.00 | 310.00 | 19840.00 | 600.00 | 38400.00 | 1505.00 | 96320.00 | 272.00 | 17408.00 | 450.00 | 28800.00 | 17408.00 | WELTECH ENGINEERS
46.00 | C Reducer 125NB-100NB Schedule 40 | 9.00 | Nos | 10.00 | 710.00 | 6390.00 | 1216.00 | 10944.00 | 2495.00 | 22455.00 | 608.00 | 5472.00 | 725.00 | 6525.00 | 5472.00 | WELTECH ENGINEERS
47.00 | C Reducer 125NB-80NB Schedule 40 | 3.00 | Nos | 10.00 | 660.00 | 1980.00 | 1159.00 | 3477.00 | 2495.00 | 7485.00 | 553.00 | 1659.00 | 800.00 | 2400.00 | 1659.00 | WELTECH ENGINEERS
48.00 | C Reducer 100 NB -80 NB Schdule 40 | 11.00 | Nos | 10.00 | 410.00 | 4510.00 | 747.00 | 8217.00 | 2080.00 | 22880.00 | 366.00 | 4026.00 | 475.00 | 5225.00 | 4026.00 | WELTECH ENGINEERS
49.00 | C Reducer 80 NB -50 NB Schdule 40 | 806.00 | Nos | 10.00 | 280.00 | 225680.00 | 579.00 | 466674.00 | 1505.00 | 1213030.00 | 212.00 | 170872.00 | 350.00 | 282100.00 | 170872.00 | WELTECH ENGINEERS
50.00 | C Reducer 80NB-25NB Schedule 40 | 5.00 | Nos | 10.00 | 320.00 | 1600.00 | 801.00 | 4005.00 | 1505.00 | 7525.00 | 280.00 | 1400.00 | 480.00 | 2400.00 | 1400.00 | WELTECH ENGINEERS
51.00 | C Reducer 50 NB -25 NB Schdule 40 | 968.00 | Nos | 10.00 | 185.00 | 179080.00 | 398.00 | 385264.00 | 1010.00 | 977680.00 | 157.00 | 151976.00 | 225.00 | 217800.00 | 151976.00 | WELTECH ENGINEERS
52.00 | Reducing Coupling 25X15 | 536.00 | Nos | 10.00 | 140.00 | 75040.00 | 474.00 | 254064.00 | 350.00 | 187600.00 | 132.00 | 70752.00 | 180.00 | 96480.00 | 70752.00 | WELTECH ENGINEERS
53.00 | Fabrication & Erection of CS pipeline: Study of layout drawngs, development of isometric or erection drawings and obtianing acceptance form NPCIL, Identification of fabricated pipe spools, handling, erection and alignment of CS piping, pipe fittings and accessories, at various elevations and locations, FME inspection, preparation of erection reports, asbuilt drawings and work completion as per approved drawings, documents and specifications. The scope also includes providing scaffolidng, temporary support arrangements, man power, material hanlding equipment such as crane / hydra, other P&M, tools & tackles and other consumables preparation of reports and submission for acceptance. | 51354.00 | Inch-Mtr | 10.00 | 460.00 | 23622840.00 | 655.00 | 33636870.00 | 885.00 | 45448290.00 | 437.00 | 22441698.00 | 440.00 | 22595760.00 | 22441698.00 | WELTECH ENGINEERS
54.00 | Welding of CS pipe: Handling, marking, cutting as per the developed drawings, removal of paint from the joint area, edge preparation, cleaning, fit up, welding using GTAW/ SMAW process as per established procedures, mechanical cleaning of weld joint, engraving, visual inspection, repair of welding if any, FME, inspection as per drawings and specification. The work also includes joint identification & marking by engraving, arranging man power, P&M, tools & tackles, all consumables including supply of welding filler wire & welding electrode of approved make, cleaning aids etc , preparation of reports and submission for accetance. Note: payment for NDE will be made in the releavant BOQ item , no separate payment for temporary supports or fixures. | 32194.00 | inch-dia | 10.00 | 1650.00 | 53120100.00 | 1883.00 | 60621302.00 | 1330.00 | 42818020.00 | 1690.00 | 54407860.00 | 1600.00 | 51510400.00 | 42818020.00 | TAP TURBO ENGINEERS PRIVATE LIMITED
55.00 | Grit blasting and supply and application of primer on pipes: Handling of CS pipes and fittings, shifting to blasting area, grit blasting using steel grits/shot, supply & application of Inorganic Zinc Silicate primer with minimum thickness(DFT) of 70 microns as per technical specification, inspection, testing, preparation of reports and work completion as per drawings, documents and specifications The scope includes assesement of material requirement, procurement of grit/shot, primer with material test certificate, inspection at contractor's store, establishment of workshop, qualification of procedures, arrangement of man power, tools & tackles, P&M, consumables, cleaning aids as per drawings and technical specifications Note : Work includes application of primer on field weld joints for pipes after Hydrotest. | 5608.00 | SqM | 10.00 | 1500.00 | 8412000.00 | 1654.00 | 9275632.00 | 740.00 | 4149920.00 | 1530.00 | 8580240.00 | 1200.00 | 6729600.00 | 4149920.00 | TAP TURBO ENGINEERS PRIVATE LIMITED
56.00 | Supply & Application of intermediate & finish paint coats on pipes : Identification of pipelines and fittings, surface cleaning, supply and application of intermediate & finish paint of Epoxy MIO intermediate coat of thickness 100 to 120 microns and two coat of Aliphatic Polyurethane painting of thickness 30 microns each on outside surface of specified color shade, inspection, preparation of reports, testing and work completion as per the drawings, documents and specification. The work scope includes assessment of material requirement, procurement with material test certificate, handling, inspection at contractor's store, establishment/arrangement of workshop, application, arrangement of man power, qualification of procedures, scaffolding and platforms, tools & tackles, P&M, consumables Note : Work includes application of paint on field weld joints for pipes after Hydrotest. Contractor shall finalise color of painting after discussion with NPCIL | 5608.00 | SqM | 10.00 | 1400.00 | 7851200.00 | 1654.00 | 9275632.00 | 445.00 | 2495560.00 | 1487.00 | 8339096.00 | 600.00 | 3364800.00 | 2495560.00 | TAP TURBO ENGINEERS PRIVATE LIMITED
57.00 | Supply, fabrication and Erection of Structural Steel: Supply of structural steel material conforming to IS 2062, E250, Quality BR consisting plates/ sheets/ angle/ channel/ beam and various profile as per IS 808, metal gratings, fasteners as per IS 1363 grade 5.6 and grade 8.8 etc, transportation, storage, handling, fabrication of pipe supports including semi clamps, U saddle, U clamps etc, fitup & welding, shifting, erection, site welding, inspection as per drawing and technical specification. This work also includes providing scaffolding / temporary platforms, man power, tools, tackles, plant and machineries, welding electrodes, other consumables and preparation of reports and submission for accpetance. | 23861.00 | kg | 10.00 | 300.00 | 7158300.00 | 313.00 | 7468493.00 | 260.00 | 6203860.00 | 255.00 | 6084555.00 | 260.00 | 6203860.00 | 6084555.00 | WELTECH ENGINEERS
58.00 | Grit blasting and supply and application of primer for support structures : Handling of supports, metal structure, shifting to blasting area, grit blasting using steel grits/shot,supply & application of Inorganic Zinc Silicate primer with minimum thickness(DFT) of 75 microns as per technical specification , inspection, testing, preparation of reports and work completion as per drawings, documents and specifications. The scope includes assesement of material requirement, procurement of grit/shot, primer with material test certificate, inspection at contractor's store, preparation of IMIR (incoming material inspection report), establishment of workshop, qualification of procedures, arrangement of man power, tools & tackles, P&M, consumables, cleaning aids etc with acceptance of EIC. Note : Work includes application of primer on field weld joints for metal structures after welding. | 25054.00 | kg | 10.00 | 50.00 | 1252700.00 | 203.00 | 5085962.00 | 40.00 | 1002160.00 | 57.00 | 1428078.00 | 30.00 | 751620.00 | 751620.00 | MGR FABRICATORS PRIVATE LIMITED
59.00 | Supply & Application of intermediate & finish paint coats on structure: Identification of metal structures, surface cleaning, supply and application of finish paint two coat of High build epoxy of thickness 80 to 90 microns on outside surface of specified color shade, inspection, preparation of reports, testing and work completion as per the drawings, documents and specification with acceptance of EIC. The work scope includes assessment of material requirement, procurement with material test certificate, handling, inspection at contractor's store, establishment of workshop, application, arrangement of man power, qualification of procedures, scaffolding and platforms, tools & tackles, P&M, consumables Note : Work includes application of paint on field weld joints for metal structures after welding. | 25054.00 | kg | 10.00 | 28.00 | 701512.00 | 236.00 | 5912744.00 | 30.00 | 751620.00 | 26.00 | 651404.00 | 17.00 | 425918.00 | 425918.00 | MGR FABRICATORS PRIVATE LIMITED
60.00 | Hydro/Pneumatic test of Piping System : Study of layout, marking and identificaiton of loops, prepration of CRR ( circuit release reports) , hydro test loops, obtaining approval from NPCIL, blanking, filling of pipeline, venting, pressurising, holding for required time, flushing, draining, drying as per drawings and specification. This work also inlcudes arranging manpower, required hydrotest manifolds, valves, calibrated safety relief valves & pressure gauges, required tools and tackles, gasket, blank and fastners, hoses, clamps, tools & tackles, P&M, scaffolding & platforms, consumables, cleaning aids etc, preparation of reports and submission for acceptance. | 51354.00 | Inch -Mtr | 10.00 | 90.00 | 4621860.00 | 165.00 | 8473410.00 | 120.00 | 6162480.00 | 81.00 | 4159674.00 | 85.00 | 4365090.00 | 4159674.00 | WELTECH ENGINEERS
61.00 | Weld Joint Inspection by RT : Identification of the weld joints, marking, radiographic examination of the weld joint by ISNT/ ASNT RT qualified personnel with all radiologial safety guide lines, developing of films, as per drawings and specification. This work also includes arrangement of man power, tools & tackles, plant & machinery, consumables, platforms, cleaning aids, arrangment of storage of source ( pit room) etc, as per drawings, preparation of reports and submission to NPCIL for acceptance along with RT film. | 296.00 | Inch dia | 10.00 | 1800.00 | 532800.00 | 1228.00 | 363488.00 | 1240.00 | 367040.00 | 1850.00 | 547600.00 | 1000.00 | 296000.00 | 296000.00 | MGR FABRICATORS PRIVATE LIMITED
62.00 | Ultrasonic Examination of weld joints: Development of procedure and technique sheets,identification of the joints, shifting the ultrasonic testing machine to the location, flush grinding the weld joint to meet the requirement, cleaning the weld joint, carrying out ultrasonic examination of weld joint by ISNT/ASNT level-II qualified personnel as per the requirements, technique sheet,drawign and technical specification,interpretation,post cleaning, preparation and submision of reports for NPCIL acceptance. This work also includes erection of scaffolding,arranging manpower, tools and tackles, calibrated UT testing machine, probes of various configuration,couplants, cleaning consumables like acetone,etc. | 741.00 | Inch dia | 10.00 | 300.00 | 222300.00 | 491.00 | 363831.00 | 1770.00 | 1311570.00 | 266.00 | 197106.00 | 500.00 | 370500.00 | 197106.00 | WELTECH ENGINEERS
63.00 | Applicable GST Rate (%) Included in the Quoted Price
| Total in Figures |  |  |  |  | 184390548.00 |  | 239461603.00 |  | 198186084.00 |  | 175522823.00 |  | 177097022.00
Lowest Amount Quoted BY: WELTECH ENGINEERS(175522823.00)

## BOQ Summary
BOQ Summary Details Tender Title: Supply, fabrication, installation of ventilation, fire fighting and Tender ID: 2026_NPCIL_267208_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | WELTECH ENGINEERS (BID ID -990032) | 175522823.00 | L1
| 2 | MGR FABRICATORS PRIVATE LIMITED (BID ID -990411) | 177097022.00 | L2
| 3 | Som Projects Pvt. Ltd. (BID ID -994255) | 184390548.00 | L3
| 4 | TAP TURBO ENGINEERS PRIVATE LIMITED (BID ID -988768) | 198186084.00 | L4
| 5 | Agnice Fire Protection Private Limited (BID ID -993000) | 239461603.00 | L5