## BoQ1
Government eProcurement System Created By: Manoj Kumar Singh Created Date/Time: 17-Jun-2026 10:48 AM Tender Title: Internal electrification of 7 no. of warehouses in CMM area including supply and installation of specified materials Tender ID: 2026_NPCIL_269370_1
Tender Inviting Authority: SM, CMM (Works Group)
Name of Work: Internal electrification of 7 no. of warehouses in CMM area including supply and installation of specified materials
Contract No: NPCIL/KK-3&4/CONST/E&I/PT/2026/22
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Sabari and Leon Electricals Pvt Ltd (GSTN-33AAGCS9735D2ZA) BID ID -1004075
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Main HT panel: Supply, installation, testing & Commissioning of 11 KV Switchgear to be located indoors, having Tinned copper bus rated for 630 A with 26.2 KA for 1 Sec, dust-proof and vermin proof, IP 54 , 14/16 gauge, CRCA sheet steel enclosure, powder coated & along with necessary hardwares and accessories and all as per specification, conforming to latest edition of relevant Bureau of Indian Standards & as approved. Incomer : 630A TP VCB - 2nos, with CT's, 2 Line PT's (separate vertical feeder), CBCT, Trivector energy meter for two incoming feeders, voltmeter, ammeter, freqency meters and micro processor based protection relays. Outgoing : 630 AMPS TP VCB - 4 nos for transformer feeder with required CT's, Bus PT with meter and protection relays, voltmeter, ammeter, freqency meters, micro processor based protection relays and transformer protection relays along with necessary hardwares & accessories etc, all as per specification . Scope includes installation of panel, positioning, alignment, panel welding, painting, Bolt nut accessories and all as required at site and all as per specification. ( 2 Line PTs , Bus PTs to be housed in separate vertical) | 1.00 | Sets |  | 5167456.00 | 5167456.00 | 5167456.00 | Sabari and Leon Electricals Pvt Ltd
2.00 | Main LT Indoor Panel Fabrication, Supply, installation, testing and commissioning of LT Indoor panel working on 440V 3-Phase & Neutral , 50Hz , AC supply. It shall be extendable at both ends, copper bus bars , fully compartmentalized , dust-proof and vermin proof, IP 54 , 14/16 gauge, CRCA sheet steel enclosure, powder coated & along with necessary hardwares and accessories and all as per specification, conforming to latest edition of relevant Bureau of Indian Standards & as approved. (Incoming cable chamber Suitable for connecting 10nos of 3.5Cx400Sqmm cable) Incomer Feeder : 1 No : 2000A 4P 50KA EDO ACB with all inbuilt protection, CT &PT , microprocessor numeric based OC and EF relay, control fuses, ammeter, voltmeter, LED indication lamps all as per IS. - 1 set Bus bar 2000A Cu, TPN tinned copper Busbar suitable for 50kA for 1 Sec Outgoing Feeders: 630A TPN Thermal magnetic MCCB -3Nos 400A TPN Thermal magnetic MCCB -2Nos 250ATPN Thermal magnetic MCCB -3No 100A TPN Thermal magnetic MCCB - 3No 63A TPN Thermal magnetic MCCB - 3No Scope includes installation of panel, positioning in concrete pedestal/ Support structure using hydra, alignment, panel welding, painting, Bolt nut accessories and all as required at site and all as per specification. (The concrete pedestal will be measured under item 38) | 1.00 | Nos. |  | 2591658.00 | 2591658.00 | 2591658.00 | Sabari and Leon Electricals Pvt Ltd
3.00 | Fabrication, Supply, installation, testing and commissioning of LT Outdoor panel working on 440V 3-Phase & Neutral , 50Hz , AC supply. It shall be extendable at both ends, copper bus bars , fully compartmentalized , dust-proof and vermin proof IP54 , 14/16 gauge, CRCA sheet steel enclosure, powder coated & along with necessary hardwares and accessories and all as per specification, conforming to latest edition of relevant Bureau of Indian Standards & as approved. (Incoming cable chamber Suitable for connecting 1R of 3.5Cx400Sqmm cable) Incomer : 630A TPN Thermal magnetic MCCB with CTs , control fuses, multifunction meter and LED indication Lamps - 1no Bus bar 630A Cu, TPN tinned copper Busbar suitable for 50kA for 1 Sec Outgoing Feeders: 250A TPN Thermal magnetic MCCB -4Nos 100A TPN Thermal magnetic MCCB -3No 63A TPN Thermal magnetic MCCB - 2No Scope includes installation of panel, positioning in concrete pedestal/ Support structure using hydra, alignment, panel welding, painting, Bolt nut accessories and all as required at site and all as per specification. (The concrete pedestal will be measured under item 38) | 1.00 | Nos. |  | 568288.00 | 568288.00 | 568288.00 | Sabari and Leon Electricals Pvt Ltd
4.00 | Fabrication, Supply, installation, testing and commissioning of LT Outdoor panel working on 440V 3-Phase & Neutral , 50Hz , AC supply. It shall be extendable at both ends, copper bus bars , fully compartmentalized , dust-proof and vermin proof IP54 , 14/16 gauge, CRCA sheet steel enclosure, powder coated & along with necessary hardware’s and accessories and all as per specification, conforming to latest edition of relevant, Bureau of Indian Standards & as approved. Incomer 250A TPN Thermal magnetic MCCB with CTs , control fuses, multifunction meter and LED indication Lamps - 1no Bus bar 250A Cu, TPN tinned copper Busbar suitable for 35kA for 1 Sec Outgoing Feeders: 100A TPN Thermal magnetic MCCB -4No 63A TPN Thermal magnetic MCCB - 5No Scope includes installation of panel, positioning in concrete pedestal/ Support structure using hydra, alignment, panel welding, painting, Bolt nut accessories and all as required at site and all as per specification. (The concrete pedestal will be measured under item 38) | 4.00 | Nos. |  | 307801.00 | 1231204.00 | 1231204.00 | Sabari and Leon Electricals Pvt Ltd
5.00 | Supply and laying of following size 11KV, XLPE insulated, Aluminium conductor, Armoured cable, insulation screened with extruded semi-conducting compound in combination with copper tape, cores laid up, inner sheath of extruded PVC sheathing, galvanised steel flat strip armoured, and overall extruded PVC sheathed cable conforming for IS:7098/II/85 with latest amendments of HT power cable. Scope includes laying of cable in excavated cable trenches, RCC hume pipes , High voltage testing and comissioning of the above cables, clamping of cable without any kinks & bend and aluminimum tag with identifcation for both side of cable and all as per specification . (Excavation will be measured under item 35 and Hume pipes will be measured under item 45)
5.10 | 3Cx300Sqmm 11KV, XLPE Aluminium Armoured cable | 2500.00 | Meter |  | 3157.00 | 7892500.00 | 7892500.00 | Sabari and Leon Electricals Pvt Ltd
5.20 | 3Cx150Sqmm 11KV, XLPE Aluminium Armoured cable | 2000.00 | Meter |  | 1908.00 | 3816000.00 | 3816000.00 | Sabari and Leon Electricals Pvt Ltd
6.00 | Supply and installation of 3C x 300 Sqmm 11KV Heat Shrinkable indoor end termination kits suitable for 11KV, XLPE Aluminium Armoured cable and all as required to complete the job in all respects, all as per specification. | 4.00 | Nos. |  | 15000.00 | 60000.00 | 60000.00 | Sabari and Leon Electricals Pvt Ltd
7.00 | Supply and installation of 3C x 300 Sqmm 11KV Heat Shrinkable outdoor end termination kits suitable for 11KV, XLPE Aluminium Armoured cable and all as required to complete the job in all respects, all as per specification. | 4.00 | Nos. |  | 20000.00 | 80000.00 | 80000.00 | Sabari and Leon Electricals Pvt Ltd
8.00 | Supply and Installation of 3C x 300Sqmm 11KV Heat Shrinkable straight through Joint kits suitable for 3CX 300sqmm, 11KV, XLPE Aluminum Armoured cable and all as required to complete the job in all respects, all as per specification. | 3.00 | Nos. |  | 30000.00 | 90000.00 | 90000.00 | Sabari and Leon Electricals Pvt Ltd
9.00 | Supply and installation of 3C x 150 Sqmm 11KV Heat Shrinkable indoor end termination kits suitable for 11KV, XLPE Aluminium Armoured cable and all as required to complete the job in all respects, all as per specification. | 2.00 | Nos. |  | 12000.00 | 24000.00 | 24000.00 | Sabari and Leon Electricals Pvt Ltd
10.00 | Supply and installation of 3C x 150 Sqmm 11KV Heat Shrinkable outdoor end termination kits suitable for 11KV, XLPE Aluminium Armoured cable and all as required to complete the job in all respects, all as per specification. | 3.00 | Nos. |  | 15000.00 | 45000.00 | 45000.00 | Sabari and Leon Electricals Pvt Ltd
11.00 | Supply and Installation of 3C x 150Sqmm 11KV Heat Shrinkable straight through Joint kits suitable for 3CX 150sqmm, 11KV, XLPE Aluminum Armoured cable and all as required to complete the job in all respects, all as per specification. | 2.00 | Nos. |  | 25000.00 | 50000.00 | 50000.00 | Sabari and Leon Electricals Pvt Ltd
12.00 | Supply and Installation of 3Cx240 Sqmm 11KV Heat Shrinkable straight through Joint kits suitable for 3CX 240 sqmm, 11KV, XLPE Aluminum Armoured cable and all as required to complete the job in all respects, all as per specification. | 2.00 | Nos. |  | 27000.00 | 54000.00 | 54000.00 | Sabari and Leon Electricals Pvt Ltd
13.00 | Supply & laying of following sizes of 1100V grade XLPE Armoured, Aluminimum/Copper cables, XLPE insulated, galvanized flat steel armoured, extruded PVC inner sheathed and outer Sheath cable conforming to IS 7098 ( Part -1). Scope includes laying of following size of Al cable in excavated trench / Hume pipes/wall/support structure, clamping of cable, cable laying without any kinks and bend, aluminimum tag with identifcation for both sides of cable etc and all as per specification . (Excavation will be measured under item 35 and Hume pipes will be measured under item 45)
13.10 | 3.5C x400 Sqmm XLPE aluminum Armoured Cable | 1500.00 | Meter |  | 2588.00 | 3882000.00 | 3882000.00 | Sabari and Leon Electricals Pvt Ltd
13.20 | 3.5C x70 Sqmm XLPE aluminum Armoured Cable | 2000.00 | Meter |  | 630.00 | 1260000.00 | 1260000.00 | Sabari and Leon Electricals Pvt Ltd
13.30 | 4C x25Sqmm XLPE aluminum Armoured Cable | 1000.00 | Meter |  | 341.00 | 341000.00 | 341000.00 | Sabari and Leon Electricals Pvt Ltd
13.40 | 4C x16 Sqmm XLPE aluminum Armoured Cable | 1000.00 | Meter |  | 267.00 | 267000.00 | 267000.00 | Sabari and Leon Electricals Pvt Ltd
13.50 | 4C x2.5 Sqmm XLPE copper Armoured Cable | 500.00 | Meter |  | 301.00 | 150500.00 | 150500.00 | Sabari and Leon Electricals Pvt Ltd
14.00 | Glanding and termination of following size of Al/Cu armoured Cable. Scope includes Supply and installation of double compression heavy duty brass cable gland with nickel plated and Suitable size Aluminum/Cu Lugs, connection, bolt nut accessories etc, and all as required at site and all as per specification.
14.10 | 3.5C x400 Sqmm XLPE aluminum Armoured Cable | 26.00 | Nos. |  | 5000.00 | 130000.00 | 130000.00 | Sabari and Leon Electricals Pvt Ltd
14.20 | 3.5C x70 Sqmm XLPE aluminum Armoured Cable | 10.00 | Nos. |  | 1500.00 | 15000.00 | 15000.00 | Sabari and Leon Electricals Pvt Ltd
14.30 | 4C x25Sqmm XLPE aluminum Armoured Cable | 30.00 | Nos. |  | 1200.00 | 36000.00 | 36000.00 | Sabari and Leon Electricals Pvt Ltd
14.40 | 4C x16 Sqmm XLPE aluminum Armoured Cable | 24.00 | Nos. |  | 1100.00 | 26400.00 | 26400.00 | Sabari and Leon Electricals Pvt Ltd
14.50 | 4C x2.5 Sqmm XLPE copper Armoured Cable | 25.00 | Nos. |  | 650.00 | 16250.00 | 16250.00 | Sabari and Leon Electricals Pvt Ltd
15.00 | Transportation, Installation, Testing and commissioning of 1000 KVA Oil type Transformer. Scope includes transportaion of transformer within kknpp 3&4 premises, erection of Transformer in existing concrete plinth, assembling, oil filteration, alignment, welding, all type of test and commissioning in site etc all as per specification. | 1.00 | Nos. |  | 50000.00 | 50000.00 | 50000.00 | Sabari and Leon Electricals Pvt Ltd
16.00 | Transportation and installation of 500KVA/250KVA outdoor package compact substation. Scope includes installation of compact substation on support structure/concrete structure, alignment, welding, welding area painting, testing & commissioing and necessary hardwares, & accessories etc., and all as required at site and all as per specification. (Support structure will be measured under item 34) | 1.00 | Nos. |  | 100000.00 | 100000.00 | 100000.00 | Sabari and Leon Electricals Pvt Ltd
17.00 | Dismantling, Transportation, Reinstallation, Testing and commissioning of 150Ah Battery charger with batteries and Floor mounted DCDB Panel. Scope includes Dismantling ,Reerection of Battery charger with batteries and Floor mounted DCDB Panel in support structure, Required Size of anchnor fasteners, assembling, alignment, welding, testing and commissioning in site etc all as per specification. (The support structure will be measured under item 34 and anchor fasteners will be measured under item 33) | 1.00 | Sets |  | 25000.00 | 25000.00 | 25000.00 | Sabari and Leon Electricals Pvt Ltd
18.00 | Supply and installation of 100W LED Flood light fitting on support structure in warehouse building. Installation scope includes Light fitting installation on support structure, Supply & laying of 3Cx1.5 sqmm copper conductor flexible cable between junction box and fixture, supply and installation of high quality PVC Glands, flexible metal hose, clamp, hardware accessories and connection etc, all as required at site and all as per specification. (The support structure will be measured under item 34) | 406.00 | Nos. |  | 3136.00 | 1273216.00 | 1273216.00 | Sabari and Leon Electricals Pvt Ltd
19.00 | Replacement of 36W recess mounted, slim type, full open, 2x2 tile SQUARE LED FITTING in place of existing 2x2 tile SQUARE LED FITTING. Scope includes removal of LED light fitting and supply & installation of 36W LED fitting in the same location and connecting the fitting with available flexible cable and all as required at site and all as per specification. | 100.00 | Nos. |  | 2181.00 | 218100.00 | 218100.00 | Sabari and Leon Electricals Pvt Ltd
20.00 | Supply and installation of equal or higher size of 150mmx150mmx75mm size of Thermo plastic junction boxes with 12nos of 4 Sqmm size wago screwless type terminal blocks for in and out circuit wire connection, mounting rail for fixing of terminal blocks and knock out opening for 25mm GI conduit etc. Installation scope includes installation of junction box on cable tray/wall, support structure, circuit identification (Circuit numbering), bolt nut accessories etc, and all as required at site and all as per specification. | 655.00 | Nos. |  | 2000.00 | 1310000.00 | 1310000.00 | Sabari and Leon Electricals Pvt Ltd
21.00 | Supply and installation of 20 A single phase - 3 PIN industrial receptacle controlled by 20A SP MCB, plug top and suitable enclosure and all as per specification | 105.00 | Nos. |  | 2000.00 | 210000.00 | 210000.00 | Sabari and Leon Electricals Pvt Ltd
22.00 | Fabrication and supply of Indoor type Main SFU feeder unit with adapter for cable in and out termination. Scope includes supply and installation of 32A TPN SFU with 32A fuse and adapter box for cable termination, Erection on support structure, welding, powder coated enclosure, suitable terminal blocks for Incoming and outgoing cable, prewired with copper wire and all as required at site and all as per specification. (The support structure will be measured under item 34) | 12.00 | Nos. |  | 10441.00 | 125292.00 | 125292.00 | Sabari and Leon Electricals Pvt Ltd
23.00 | Supply, laying, testing and commissioning of power circuit wiring (3Run x 4 Sq.mm) PVC insulated FRLSH multistranded copper wire 1100V grade in open/wall/perforated tray/warehouse support structure/ 25mm heavy duty GI conduits. Scope includes supply of wires and terminal lugs, rigid 25mm GI conduit with necessary bends, junctions, GIclamps with spacers, supply and laying of 14 swg copper bare wire, laying throughout GI conduit, clamping of copper wire on conduit by using copper clamps, connection and hardware accessories etc. (From PDB to Power receptacle, Receptacle to receptacle, PDB to Exhaust Fan) | 17500.00 | Meter |  | 580.00 | 10150000.00 | 10150000.00 | Sabari and Leon Electricals Pvt Ltd
24.00 | Supply, laying, testing and commissioning of light circuit wiring (3Run x 2.5 Sq.mm) PVC insulated FRLSH multistranded copper wire 1100V grade in open/wall/perforated tray/warehouse support structure/ 25mm heavy duty GI conduits. Scope includes supply of wires and terminal lugs, rigid 25mm GI conduit with necessary bends, junctions, GI clamps with spacers, supply and laying of 14 swg copper bare wire, laying throughout GI conduit, clamping of copper wire on conduit by using copper clamps, connection and hardware accessories etc,. (From LDB to Light Fixture, Light fitting to Light fitting) | 6500.00 | Meter |  | 514.00 | 3341000.00 | 3341000.00 | Sabari and Leon Electricals Pvt Ltd
25.00 | Fabrication, supply, installation & commissioning of various type of double door Outdoor distribution board, incorporating tinned copper busbar, CRCA sheet enclosure, powder coated, suitable screwless terminal blocks for Incoming and outgoing cable, 10% additional outgoing terminal for future circuits, suitable size of earth busbar, prewired with copper wire, suitable knockout opening for conduit and cable entry and hardware accessories etc . scope includes installation on existing support structure , DB identification, danger sticker hardware accessories etc, all as per specification conforming to latest edition of relevant, Bureau of Indian standards. (Support fabrication will be measured under item 34)
25.10 | Distribution board Incoming : 100A TPN RCBO with 30ma sensitivity - 1 no 100A TPN Tinned copper BUSBAR 32A DP MCB -3 Nos Outgoing : 20A SP MCB -15 nos | 7.00 | Nos. |  | 56697.00 | 396879.00 | 396879.00 | Sabari and Leon Electricals Pvt Ltd
25.20 | Distribution board Incoming : 100A TPN RCBO with 30ma sensitivity - 1 no 100A TPN Tinned copper BUSBAR Outgoing : 20A SP MCB -18 nos | 7.00 | Nos. |  | 52600.00 | 368200.00 | 368200.00 | Sabari and Leon Electricals Pvt Ltd
26.00 | Cable Trays Supply and Installation of following size of perforated type Hot dip GI trays to carry lighting circuit in warehouse building . Scope includes supply of straight tray, necessary bend, Tees, elbows, reducers, connecting plate, fixing of cable tray on support structures of warehouse building approximately 15mtrs height, welding, cutting, painting etc to complete the job in all aspects as required at site and all as per specification. (The support structures shall be measured under item 34)
26.10 | 200 x 50mm perforated type cable Tray | 1600.00 | Meter |  | 1143.00 | 1828800.00 | 1828800.00 | Sabari and Leon Electricals Pvt Ltd
26.20 | 150x 50mm perforated type cable Tray | 1300.00 | Meter |  | 932.00 | 1211600.00 | 1211600.00 | Sabari and Leon Electricals Pvt Ltd
26.30 | 100 x50 mm perforated type cable Tray | 900.00 | Meter |  | 786.00 | 707400.00 | 707400.00 | Sabari and Leon Electricals Pvt Ltd
26.40 | 75x 50mm perforated type cable Tray | 650.00 | Meter |  | 648.00 | 421200.00 | 421200.00 | Sabari and Leon Electricals Pvt Ltd
27.00 | Supply & installation of 40 mm dia, 3 mtr long MS rod for earthing of panels. Scope includes supply and installation of the rods directly driven into earth, hole to be filled with bentonite powder and welding connection between the rod and earth flat, welding area painting, 2x2 feet square RCC concrete chamber with top cover for earth pit, painting of earth pit chamber, identification, MS rod expose area painting work etc and all as per specification. | 16.00 | Nos. |  | 10000.00 | 160000.00 | 160000.00 | Sabari and Leon Electricals Pvt Ltd
28.00 | Supply and installation of following size GI flat. Installation includes welding of flats, clamping of flats in wall using anchor fastener, welding on support structure and welding area painting etc, all as per specification. (The anchor fasteners will be measured under item 33)
28.10 | 50X10mm GI Flat | 150.00 | Meter |  | 600.00 | 90000.00 | 90000.00 | Sabari and Leon Electricals Pvt Ltd
28.20 | 50X6mm GI Flat | 500.00 | Meter |  | 300.00 | 150000.00 | 150000.00 | Sabari and Leon Electricals Pvt Ltd
28.30 | 25X6mm GI Flat | 450.00 | Meter |  | 175.00 | 78750.00 | 78750.00 | Sabari and Leon Electricals Pvt Ltd
28.40 | 25X3mm GI Flat | 100.00 | Meter |  | 100.00 | 10000.00 | 10000.00 | Sabari and Leon Electricals Pvt Ltd
29.00 | Supply and Laying of single core 16 sqmm flexible copper bare conductor for earthing. Scope includes laying of copper conductor wherever earthing point is required like Junction box, Adapter box, LDB and wall mounted panels, and all as required to complete the job in all respects. | 40.00 | Meter |  | 250.00 | 10000.00 | 10000.00 | Sabari and Leon Electricals Pvt Ltd
30.00 | Termination of single core 16 sqmm flexible copper bare conductor cable for earthing. Scope includes supply of 2nos of ring type copper lugs each side for earth point connection, crimping of 16 sqmm lugs, bolt nuts accessories etc, all as required to complete the job in all respects. | 25.00 | Nos. |  | 200.00 | 5000.00 | 5000.00 | Sabari and Leon Electricals Pvt Ltd
31.00 | Supply and installation of 100mm Size of Heavy duty GI pipe for laying of cable. Scope also includes installation of pipe on wall, support by using GI clamps, laying in excavated trench etc, all as per specification . (Excavation will be measured under 35) | 50.00 | Meter |  | 1700.00 | 85000.00 | 85000.00 | Sabari and Leon Electricals Pvt Ltd
32.00 | Supply and installation of 50mm Size of Heavy duty GI pipe for laying of cable. Scope also includes installation of pipe on wall, support by using GI clamps, laying in excavated trench etc, all as per specification . (Excavation will be measured under item 35) | 50.00 | Meter |  | 800.00 | 40000.00 | 40000.00 | Sabari and Leon Electricals Pvt Ltd
33.00 | Supply and Installation of 8mm GI anchor fasteners for support erection work and as required at site to complete the job in all respects, suitable for concrete structures. | 2000.00 | Nos. |  | 100.00 | 200000.00 | 200000.00 | Sabari and Leon Electricals Pvt Ltd
34.00 | Providing, fabricating and erection of Structural steel members made out of M.S angles, ISMC channel, ISMC flats, chequred plates, pipes, channels, tubes , rods, etc conforming to relevant IS etc, including anchor fasteners for support erection, cost of welding, welding rods, drilling holes, bolts / nuts wherever required and providing and applying two or more coats of approved quality synthetic enamel paint over a coat of zinc chromate yellow primer etc, as per drawing and specifications . (Anchor fasteners will be measured under item 33) | 32.00 | MT |  | 180.00 | 5760.00 | 5760.00 | Sabari and Leon Electricals Pvt Ltd
35.00 | Earth work excavation by mechanical means(hydraulic excavator)/manual means in Soft rock in over areas, raft etc. including shoring, shrutting wherever required bailing/pumping of water, leveling the bottom of excavation and refilling selected excavated materials and consolidating in the sides of foundation and disposing the surplus materials at places as directed within a lead of 2 Kms all as per drawings and specifications. | 2000.00 | Cu. Meter |  | 500.00 | 1000000.00 | 1000000.00 | Sabari and Leon Electricals Pvt Ltd
36.00 | Supply and placing in position Fly ash bricks for cable protection as directed (18nos per mtrs) | 50000.00 | Nos. |  | 12.00 | 600000.00 | 600000.00 | Sabari and Leon Electricals Pvt Ltd
37.00 | Providing and Laying plain cement concrete 1:2:4, using 20mm and down graded stone aggregate at all height including mechanical mixing, levelling, compaction , vibrating, finishing smooth the exposed surfaces of concrete, curing etc complete and all as required at site and standards specification | 15.00 | Cu. Meter |  | 13000.00 | 195000.00 | 195000.00 | Sabari and Leon Electricals Pvt Ltd
38.00 | Providing, cutting, bending, placing and tying mild steel, high yield steel reinforcement in RCC works including providing spacer blocks in CM 1:2, binding wires etc. complete at all elevations as per requirements including dewatering wherever necessary etc complete and as required at site and as per specifications (Plinth for panel and Compact substation) | 1.00 | MT |  | 160000.00 | 160000.00 | 160000.00 | Sabari and Leon Electricals Pvt Ltd
39.00 | Casting, supply and installation of 450 X 300 X 75 mm pre cast covers with "HT cable" engravement for HT cable. Casting of slab will be done with 6 mm rod 125 mm spacing bothways, 1:2:4 mix & fine finish with cement mortar, all as per specification . | 2000.00 | Nos. |  | 500.00 | 1000000.00 | 1000000.00 | Sabari and Leon Electricals Pvt Ltd
40.00 | Providing and filling /spreading Crusher sand 30mm thick (compacted thickness) for preparation of base to lay interlocking precast concrete paver blocks including, leveling, placing, to the required slope, compacting with roller etc complete as per drawings and specifications. (Payment shall be made only for compacted thickness) | 100.00 | Cu. Meter |  | 4000.00 | 400000.00 | 400000.00 | Sabari and Leon Electricals Pvt Ltd
41.00 | Providing and laying plain cement concrete 1:4:8 using 40 mm and down graded stone aggregate at all height including mechanical mixing, leveling, compaction, vibrating, shuttering, finishing smooth the exposed surfaces of concrete, curing etc complete as per drawings and standard specifications. | 120.00 | Cu. Meter |  | 10000.00 | 1200000.00 | 1200000.00 | Sabari and Leon Electricals Pvt Ltd
42.00 | Providing and constructing fly ash brick masonry in CM 1:6, using fly ash bricks as per IS:12894, class designation : 5 from the manufacturer approved by NPCIL, including scaffolding, curing and racking out joints etc complete as per specifications and drawings. | 20.00 | Cu. Meter |  | 10000.00 | 200000.00 | 200000.00 | Sabari and Leon Electricals Pvt Ltd
43.00 | Plastering of external faces of brick work/concrete at all elevations in cement mortar 1:4, 20 mm thick including scaffolding, curing, forming grooves, plaster bands, border, keystone etc wherever required all as per drawings and specifications | 100.00 | Sq. Meter |  | 500.00 | 50000.00 | 50000.00 | Sabari and Leon Electricals Pvt Ltd
44.00 | Providing and Fixing chain link fencing to M S Angle posts using PVC coated GI wire chain link fencing 50x50x9 G as per IS-2721 using TATA or equivalent make GI wire, with 6 mm dia MS rods tied vertically on posts including providing PVC coated 4 mm dia GI wire horizontally at top and bottom, 6mm dia MS rods tied vertically on posts using 16G G.I annealed binding wire etc., complete as per drawings and specifications | 100.00 | Sq. Meter |  | 1500.00 | 150000.00 | 150000.00 | Sabari and Leon Electricals Pvt Ltd
45.00 | Supply and installation of NP -2 class RCC hume pipe of size 300 mm dia, with collars, cementing has to be done wherever collar is used etc, all as per specification . (excavation will be measured in item 35) | 50.00 | Meter |  | 1500.00 | 75000.00 | 75000.00 | Sabari and Leon Electricals Pvt Ltd
46.00 | Supply and installation of Cable route markers with 35x35x6mm plate with 1mtrs long angle and HT & LT cable identification for underground cables routes. Scope includes supply and installation of cast iron route markers with 200x200x200mm size 1:2:4 concrete base, painting the marker red background and white arrow identification and installation of route marker on existing cable route area etc, and all as required at site and as per specification.(for UG LT &HT Power Cable) | 150.00 | Nos. |  | 1500.00 | 225000.00 | 225000.00 | Sabari and Leon Electricals Pvt Ltd
47.00 | Supply and installation of 1000mm wide 3mm thick rubber mats for 11KV panels and LV panels as per IS15632. Installation scope includes cleaning the area, applying adhesive suitable for rubber mat, laying of rubber mat etc. and all as required at site and as per specification. | 50.00 | Sq. Meter |  | 1500.00 | 75000.00 | 75000.00 | Sabari and Leon Electricals Pvt Ltd
48.00 | Supply and installation of different sizes of GI Bolts nuts & accessories, GI Full Threaded Rods, other GI materials etc to complete the job in all as required at site and all as per specification. | 500.00 | Kgs |  | 300.00 | 150000.00 | 150000.00 | Sabari and Leon Electricals Pvt Ltd
49.00 | Dismantling, Transportation and Erection of 11mtrs height Four pole structure along with PIN & DISC insulators, DOG conductors . Scope includes dismantling and Re-erection of 11mtrs height Four pole structure with all supports, Four pole structure with line materials shifting from existing location to new location, dismantling & Re-erection of 11KV grade PIN & DISC insulator with accessories on pole structure, supply of required size T & PAD connectors for ACSR conductor/HT cable tapping point connection, Dog conductor double busbar arrangement for cable tapping point of 4 pole structure, jumpering work, pole painting of single coat aluminum paint and necessary hardwares & accessories etc, all as per specification and all as required at site. | 1.00 | Sets |  | 100000.00 | 100000.00 | 100000.00 | Sabari and Leon Electricals Pvt Ltd
50.00 | Supply & installation of 11KV, 800 Amps off-load, double break, gang operated switch with Earth Switch. Scope includes supply of above switch with all accessories, Erection on existing Four pole structure, safety interlock provided in between line switch and earth switch, GI pipe with handle for switch operation, marking of handle, dog conductor connection, alignment of switch and necessary hardwares & accessories etc, all as required at site and all as per specification. | 2.00 | Sets |  | 40000.00 | 80000.00 | 80000.00 | Sabari and Leon Electricals Pvt Ltd
51.00 | Providing and using JCB for bush Clearance , OH line area cleaning, Substation surrounding area cleaing, leveling & dozing the undulated area mechanically and the rate is inclusive of lubricants fuel and operator and hire charges of machinery including disposing off debris up to lead of 2km as directed. | 50.00 | Hrs |  | 2000.00 | 100000.00 | 100000.00 | Sabari and Leon Electricals Pvt Ltd
52.00 | Supply, Installation and commissioning of 250 W LED flood light luminaries with complete set for outdoor application. Scope includes erection of LED fitting in building roof top,wall, support structure, cable termination, required size of supply & installation of anchor fasteners and hardware accessories etc, and all as per specification. (The anchor fasteners will be measured under item 33) | 100.00 | Nos. |  | 8128.00 | 812800.00 | 812800.00 | Sabari and Leon Electricals Pvt Ltd
53.00 | Applicable GST Rate (%) Included in the Quoted Price
| Total in Figures |  |  |  |  | 56938253.00
Lowest Amount Quoted BY: Sabari and Leon Electricals Pvt Ltd(56938253.00)

## BOQ Summary
BOQ Summary Details Tender Title: Internal electrification of 7 no. of warehouses in CMM area including supply and installation of specified materials Tender ID: 2026_NPCIL_269370_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Sabari and Leon Electricals Pvt Ltd (BID ID -1004075) | 56938253.00 | L1