## BoQ1
Government eProcurement System Created By: RAJESHKUMAR G Pillai Created Date/Time: 09-Sep-2026 05:20 PM Tender Title: Works contract for supply, installation, testing and commissioning of 256 ton capacity VRF/VRV chilled air system in documentation center for KKNPP-1 to 6. Tender ID: 2026_NPCIL_277826_1
Tender Inviting Authority: Senior Manager(CMM-Works Group)
Name of Work: Works contract for supply, installation, testing and commissioning of 256 ton capacity VRF/VRV chilled air system in documentation center for KKNPP-1 to 6.
Tender No: NPCIL/KK-1-6/E&US/ELECTRICAL-INFRA/PT/2026/54
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SREE RAGAVENDRA INDUSTRIAL ENGINEERS (GSTN-33AAJPR4590F1ZJ) BID ID -1029569
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of Modular type Variable Refrigerant Flow/Variable Refrigerant Volume air cooled Outdoor units suitable for cooling/heating having 100% hermetically sealed inverter type twin Rotary/Scroll Compressor(s), minimum two compressors (with individual seperate PCB) for above 14HP modules, microprocessor based Controller, top discharge type condensing unit(s), with R-410-A Refrigerant or equivalent, vibration Isolators with suitable foundation etc. complete as required. To have better efficiency condensor fan shall be capable to operate at different speed with respect to load. The unit shall deliver the rated capacity and in confirmation as per IS 18728:2024 and CPWD Specifications and work even at 50°C ambient temperature without tripping. The system shall be able to deliver 100% of the rated capacity upto 39 Degree Celcius. The unit shall be suitable to work on 400V +/- 10%, 3 Phase, 50Hz AC power supply and BMS compatible. The unit shall be filled with first charge of the refrigerant and ready for use as required. The condenser should be coated with a hydrophilic film to prevent water accumulation on the surface of the heat exchanger, enhance water dispersion, and reduce the risk of degradation, thereby improving overall performance and durability. The Indian Seasonal Energy Efficiency Ratio (ISEER) of the unit shall be as per Energy Conservation and Sustainable Building Code (ECSBC) 2024 as below and complete as per CPWD specification, connections, inter connections etc. as required. (For capacity <40 kWr ISEER 5.4, Capacity > 40 and <70 ISEER 5.5, Capacity > 70 ISEER 5.6 for ECSBC Building) | 16.00 | Nos. |  | 442843.00 | 7085488.00 | 7085488.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
2.00 | Supply, Installation, Testing and Commissioning of 8TR capacity and external static pressure VRF/VRV ceiling mounted mid high static ductable type Indoor unit equipped with washable synthetic media prefilter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, corded remote control, outer cabinet, vibration Isolators, drain pan, drain pump, other necessary supports etc., suitable for operation on single phase AC supply 230 V ± 10%, 50 Hz complete as required. The Indoor units must shut down upon receiving a singal from the BMS System/Fire Signals. The system shall be capable to adjust air flow as per room requirement automatically. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. (Make will be same as of Outdoor) High Static Ductable units (minimum 49 to 77 Pascal external static pressure) | 32.00 | Nos. |  | 115307.00 | 3689824.00 | 3689824.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
3.00 | Supply, Fabrication, installation and testing of 1.0mm thickness galvanised sheet steel metal ducts (FACTORY FABRICATED DUCTS) in accordance with the approved shop drawings complete with all accessories like vanes, flanges, suspension rods , anchor bolts, GI bolts & nuts, canvas connections , duct dampers & splitter dampers etc.,and as required | 3000.00 | Sq.Meter |  | 2031.00 | 6093000.00 | 6093000.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
4.00 | Supply and Installation of 1 ½ inch PVC Drain pipe with necessary accessories including Insulation for connection to indoor unit and its connecting to common drain point. | 650.00 | Meter |  | 314.00 | 204100.00 | 204100.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
5.00 | Supply, Installation, testing and commissioning including vaccumization and Nitrogen testing of 9.5 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XPLE Class-O tubular insulation/with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of 19 mm thick insulation as given below for Suction and Liquid lines, all accessories as per specifications etc. as required | 200.00 | Meter |  | 700.00 | 140000.00 | 140000.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
6.00 | Supply, Installation, testing and commissioning including vaccumization and Nitrogen testing of 22.2 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XPLE Class-O tubular insulation/with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of 19 mm thick insulation as given below for Suction and Liquid lines, all accessories as per specifications etc. as required | 200.00 | Meter |  | 1467.00 | 293400.00 | 293400.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
7.00 | Supply, Installation, testing and commissioning including vaccumization and Nitrogen testing of 15.86 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XPLE Class-O tubular insulation/with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of 19 mm thick insulation as given below for Suction and Liquid lines, all accessories as per specifications etc. as required | 1100.00 | Meter |  | 1286.00 | 1414600.00 | 1414600.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
8.00 | Supply, Installation, testing and commissioning including vaccumization and Nitrogen testing of 28.58 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XPLE Class-O tubular insulation/with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of 19 mm thick insulation as given below for Suction and Liquid lines, all accessories as per specifications etc. as required | 1100.00 | Meter |  | 2231.00 | 2454100.00 | 2454100.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
9.00 | Supply,installation of GI Trunking Tray constructed from 16G GSS, MS L angle support for Tray, covered with 16G GI sheet cover for all exposed copper refrigerant pipes. | 1500.00 | Sq.Meter |  | 1516.00 | 2274000.00 | 2274000.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
10.00 | Supply, Installation, Testing and Commissioning of Y/T/Multi Joints in indoor units. Joints shall be of same Original Equipment Manufacturer (OEM) make as of ODUs and IDUs | 64.00 | nos. |  | 5723.00 | 366272.00 | 366272.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
11.00 | Supply, installation, testing & commissioning of LT Panel fabricated out of 16/14 gauge CRCA sheet steel in a cubicle compartmentalized free standing floor/wall mounted, dust & vermin proof with reinforcement of suitable size angle iron channel and or flats wherever necessary. Panel shall be treated with all anti- corrosive process before painting as per specifications with 2coats of zinc chromate primer & final approved shade of powder coated paint. 2nos of earthing terminals shall be provided for all panels. Panels shall be suitablefor415volts, 50Hz, 3phase, 4wire, supply system. Lifting hooks shall also be provided for panel. Bus bar: 400 A TPN Aluminium bus bar Incoming: 4pole 400A MCCB of Microprocessor release with over current, earth fault and short circuit protection with adjustable current and time setting, additional Shunt release to trip the MCCB through earth leakage relay connected to CBCT of 30/5A for sensitive earth fault protection, Phase CT of 400/5A for measurement, Multifunction meter, Indication lamp-R, Y, B, Outgoing: 40 A TPN MCB - 10 no’s, 63A TPN MCB-4 no’s including terminations of cables. | 2.00 | Nos. |  | 390103.00 | 780206.00 | 780206.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
12.00 | supply and installation of 1 sq.mm twin circular, FRLS PVC sheathed workshop flexible cable (signalling cable for connection between indoor to outdoor unit ) | 1500.00 | Meter |  | 223.00 | 334500.00 | 334500.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
13.00 | Supplying and fixing of 415 V horitzontal type 6 way, (4+18) TPN, prewired MCB DB with extended loose wire box, double door, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including termination of cables, earthing etc. as required. | 4.00 | Nos. |  | 37672.00 | 150688.00 | 150688.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
14.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 2000.00 | Meter |  | 67.00 | 134000.00 | 134000.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
15.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 250.00 | Meter |  | 185.00 | 46250.00 | 46250.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
16.00 | Providing and Installation of 2P MCB 6-32A in existing DB's / panels including termination as required | 36.00 | Nos. |  | 2280.00 | 82080.00 | 82080.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
17.00 | Providing and Installation of 4P MCB 63A in existing DB's / panels including termination as required | 4.00 | Nos. |  | 4383.00 | 17532.00 | 17532.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
18.00 | Providing and fixing 6SWG dia GI wire on surface or in recess for loop earthing as required | 500.00 | Meter |  | 58.00 | 29000.00 | 29000.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
19.00 | Supply and fixing of powder coated extruded Aluminium supply air grills with air flow volume control damper | 100.00 | Sq.Meter |  | 15526.00 | 1552600.00 | 1552600.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
20.00 | Supply and fixing of powder coated extruded Aluminium return air grills with louvers but without volume control dampers complete as required | 75.00 | Sq.Meter |  | 13773.00 | 1032975.00 | 1032975.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
21.00 | Supplying and fixing 50 mm thick aluminium foil faced resin bonded fibre glass insulation (on duct ) of density 24 kg/cu.m or mineral wool insulation(non combustible) of density 44 kg/cu m after applying two coats of cold setting adhesive (CPRX compound) sealing all joints with self adhesive aluminium tape & covering with 0.63mmx19mm GI wire mesh netting butting all joints and laced with GI wire complete as per specifications and as required. (for indoor applications). | 650.00 | Sq.Meter |  | 775.00 | 503750.00 | 503750.00 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS
22.00 | Applicable GST Rate (%) Included in the Quoted Price
| Total in Figures |  |  |  |  | 28678365.00
Lowest Amount Quoted BY: SREE RAGAVENDRA INDUSTRIAL ENGINEERS(28678365.00)

## BOQ Summary
BOQ Summary Details Tender Title: Works contract for supply, installation, testing and commissioning of 256 ton capacity VRF/VRV chilled air system in documentation center for KKNPP-1 to 6. Tender ID: 2026_NPCIL_277826_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SREE RAGAVENDRA INDUSTRIAL ENGINEERS (BID ID -1029569) | 28678365.00 | L1