## BoQ1
Government eProcurement System Created By: Pankaj Malik Created Date/Time: 25-Mar-2026 04:26 PM Tender Title: SITC of 11 KV RMU outdoor panel with associated work in Surface Installations of Jorhat Asset Tender ID: 2026_ONGC_264644_1
Tender Inviting Authority: Pankaj Malik, SE(Electronics) malik_pankaj@ongc.co.in / singhal_aditya@ongc.co.in, contact details: 9968602180 / 9968282476 / 0376-2708169
Name of Work: SITC of 11 KV RMU outdoor panel with associated work in Surface Installations of Jorhat Asset
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Item Code | Power Tools and Engineering (GSTN-18ABSPJ6782F2Z1) BID ID -984150 |  | BORA ELECTRICALS (GSTN-NA) BID ID -980162
[5 empty] | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | L1 Rate Without Tax | L1 Bidder Without Tax | L1 Rate With Tax | L1 Bidder With Tax
1.00 | RMU and remote control panel
1.01 | Design, manufacture, manufacturer’s factory testing, supply, installation, and commissioning of 630A, 11 KV, Ring Main Unit (RMU) Outdoor type with VCB, SF6 gas-insulated switchgear panel complete with all accessories including associated equipment. Panel fabricated out of min. 2 mm thick CRCA powder (minimum thickness of powder coating shall be 80 micron) coated.The outdoor RMU panel to be complete with its panel, CTs (30:5/1), PTs and numerical protection relays such as overcurrent/earth fault, under voltage/overvoltage relays, broken conductor protection, DC supply monitoring relay, Master trip relay, Auxiliary relays for transformer protections such as buchholz (alarm &trip). The panel may also have an in-built DC power pack for providing control supply for control & protection. (As per ONGC specification) | 3.00 | Nos | item1 | 1485660.00 | 1753078.80 | 1972881.00 | 2327999.58 | 1485660.00 | Power Tools and Engineering | 1753078.80 | Power Tools and Engineering
1.02 | Supply, fixing, testing and commissioning of indoor mounting control panel dust and vermin proof wall mounting, fabricated out of min. 2 mm thick CRCA powder coated sheet steel suitable for use at 110V DC/ 24V DC with ON/OFF/TRIP (Red/Green/Amber) LED indicating lamps, DC supply healthy indicating lamp, ON/OFF push button with 2A SP MCB backup protection with din bar, terminal along with interconnections with 2.5 sq mm flexible unarmoured copper wire. | 3.00 | Nos | item2 | 743160.00 | 876928.80 | 30762.00 | 36299.16 | 30762.00 | BORA ELECTRICALS | 36299.16 | BORA ELECTRICALS
2.00 | Supply of cable
2.01 | Supply of 3C ×95 sq mm 11 KV grade armoured cross linked polyethylene cable(aluminium) | 240.00 | M | item3 | 204240.00 | 241003.20 | 307200.00 | 362496.00 | 204240.00 | Power Tools and Engineering | 241003.20 | Power Tools and Engineering
2.02 | Supply of 10C×2.5 sq mm XLPE insulated (Heavy Duty) armoured electrical control cable with copper conductor for working voltage upto & including 1.1 KV conforming to IS:7098/Part-I with latest amendments, Make: Gemscab/Havells/ RR-kabel /NICCO/ Grandlay/Glostar/finolex/HPL/Delton/Plaza/KEI/Polycab. | 200.00 | M | item4 | 87600.00 | 103368.00 | 97200.00 | 114696.00 | 87600.00 | Power Tools and Engineering | 103368.00 | Power Tools and Engineering
2.03 | Supply of 4x2.5 sq mm XLPE insulated armoured electrical cable with copper conductor for working voltage upto & including 1.1 KV conforming to IS:7098/Part-I with latest amendments, Make: Gemscab/Havells/ RR-kabel /NICCO/ Grandlay/Glostar/finolex/HPL/Delton/Plaza/KEI/Polycab. | 280.00 | M | item5 | 53480.00 | 63106.40 | 62440.00 | 73679.20 | 53480.00 | Power Tools and Engineering | 63106.40 | Power Tools and Engineering
3.00 | Cable laying (HV)
3.01 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. 8.1.1 Upto 120 sq. mm | 90.00 | M | item6 | 22500.00 | 26550.00 | 42750.00 | 50445.00 | 22500.00 | Power Tools and Engineering | 26550.00 | Power Tools and Engineering
3.02 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required Upto 120 sq. mm | 90.00 | M | item7 | 22500.00 | 26550.00 | 29340.00 | 34621.20 | 22500.00 | Power Tools and Engineering | 26550.00 | Power Tools and Engineering
3.03 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required Upto 120 sq. mm . | 60.00 | M | item8 | 15000.00 | 17700.00 | 4200.00 | 4956.00 | 4200.00 | BORA ELECTRICALS | 4956.00 | BORA ELECTRICALS
4.00 | Cable laying (MV)
4.01 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required Upto 35 sq. mm | 250.00 | M | item9 | 62500.00 | 73750.00 | 89000.00 | 105020.00 | 62500.00 | Power Tools and Engineering | 73750.00 | Power Tools and Engineering
4.02 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required Upto 35 sq. mm | 170.00 | M | item10 | 42500.00 | 50150.00 | 41820.00 | 49347.60 | 41820.00 | BORA ELECTRICALS | 49347.60 | BORA ELECTRICALS
4.03 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required Upto 35 sq. mm | 45.00 | M | item11 | 11250.00 | 13275.00 | 1575.00 | 1858.50 | 1575.00 | BORA ELECTRICALS | 1858.50 | BORA ELECTRICALS
4.04 | Laying and fixing of one number PVC insulated and PVCsheathed / XLPE power cable of 1.1 KV grade of following sizeon wall surface as required Upto 35 sq. mm (clamped with 1mm thick saddle) | 15.00 | M | item12 | 3750.00 | 4425.00 | 780.00 | 920.40 | 780.00 | BORA ELECTRICALS | 920.40 | BORA ELECTRICALS
5.00 | Civil works
5.01 | Excavation for cable trenches in soft soil, depth upto 1.2 m including dressing of sides lift upto 1.5 m, including getting out the excavated soil, refilling with sand and or good soil after laying of cable/ pipe etc in layers of 20 cm, ramming, watering and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 6.00 | CUM | item13 | 30000.00 | 35400.00 | 3534.00 | 4170.12 | 3534.00 | BORA ELECTRICALS | 4170.12 | BORA ELECTRICALS
6.00 | HV CABLE JOINTING & END TERMINATION
6.01 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required Upto 35 sq. mm | 6.00 | Each | item14 | 5610.00 | 6619.80 | 78816.00 | 93002.88 | 5610.00 | Power Tools and Engineering | 6619.80 | Power Tools and Engineering
6.02 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required Upto 35 sq. mm | 6.00 | Each | item15 | 6966.00 | 8219.88 | 98658.00 | 116416.44 | 6966.00 | Power Tools and Engineering | 8219.88 | Power Tools and Engineering
6.03 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required Upto 35 sq. mm | 1.00 | Each | item16 | 3415.00 | 4029.70 | 26267.00 | 30995.06 | 3415.00 | Power Tools and Engineering | 4029.70 | Power Tools and Engineering
7.00 | Earthing
7.01 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required Upto 35 sq. mm | 6.00 | Each | item17 | 60000.00 | 70800.00 | 43218.00 | 50997.24 | 43218.00 | BORA ELECTRICALS | 50997.24 | BORA ELECTRICALS
7.02 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required Upto 35 sq. mm | 30.00 | Metre | item18 | 6300.00 | 7434.00 | 9030.00 | 10655.40 | 6300.00 | Power Tools and Engineering | 7434.00 | Power Tools and Engineering
7.03 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required Upto 35 sq. mm | 12.00 | Metre | item19 | 900.00 | 1062.00 | 1572.00 | 1854.96 | 900.00 | Power Tools and Engineering | 1062.00 | Power Tools and Engineering
7.04 | Laying and fixing of one number PVC insulated and PVCsheathed / XLPE power cable of 1.1 KV grade of following sizeon wall surface as required Upto 35 sq. mm (clamped with 1mm thick saddle) | 20.00 | Metre | item20 | 3500.00 | 4130.00 | 940.00 | 1109.20 | 940.00 | BORA ELECTRICALS | 1109.20 | BORA ELECTRICALS
8.00 | Cable glands
8.01 | Supply and fixing of Brass compression gland for (25 mm) 10X 2.5sq. mm 1.1 KV grade cable with making of hole in cubicle panel | 6.00 | Nos | item21 | 1116.00 | 1316.88 | 1398.00 | 1649.64 | 1116.00 | Power Tools and Engineering | 1316.88 | Power Tools and Engineering
8.02 | Supply and fixing Brass compression gland (19 mm) for 3 X 2.5 sq. mm 1.1 KV grade cable with making of hole in cubicle panel | 6.00 | Nos | item22 | 786.00 | 927.48 | 684.00 | 807.12 | 684.00 | BORA ELECTRICALS | 807.12 | BORA ELECTRICALS
9.00 | Cable route marker
9.01 | Supplying and fixing cable route marker with 10 cm X 10 cm X 5 mm thick G.I. plate with inscription there on, bolted /welded to 35 mm X 35 mm X 6 mm angle iron, 60 cm long and fixing the same in ground as required. | 15.00 | Each | item23 | 7500.00 | 8850.00 | 7050.00 | 8319.00 | 7050.00 | BORA ELECTRICALS | 8319.00 | BORA ELECTRICALS
10.00 | Distribution Board & Blinking Plate
10.01 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 4 way (4 + 12), Double door | 6.00 | Each | item24 | 39480.00 | 46586.40 | 12966.00 | 15299.88 | 12966.00 | BORA ELECTRICALS | 15299.88 | BORA ELECTRICALS
11.00 | Blanking plate
11.01 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 12.00 | Each | item25 | 25200.00 | 29736.00 | 156.00 | 184.08 | 156.00 | BORA ELECTRICALS | 184.08 | BORA ELECTRICALS
12.00 | MCB
12.01 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load offollowing poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Double pole | 6.00 | Each | item26 | 2700.00 | 3186.00 | 3660.00 | 4318.80 | 2700.00 | Power Tools and Engineering | 3186.00 | Power Tools and Engineering
12.02 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load offollowing poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Triple pole and neutral | 6.00 | Each | item27 | 5886.00 | 6945.48 | 7638.00 | 9012.84 | 5886.00 | Power Tools and Engineering | 6945.48 | Power Tools and Engineering
13.00 | RCCB
13.01 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required 25 A | 3.00 | Each | item28 | 5973.00 | 7048.14 | 7245.00 | 8549.10 | 5973.00 | Power Tools and Engineering | 7048.14 | Power Tools and Engineering
14.00 | Wiring
14.01 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required: 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 15.00 | Metre | item29 | 7725.00 | 9115.50 | 3945.00 | 4655.10 | 3945.00 | BORA ELECTRICALS | 4655.10 | BORA ELECTRICALS
14.02 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with piano type switch, phenolic laminated sheet, suitable size M.S. box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc. as required: Group A | 6.00 | Point | item30 | 3090.00 | 3646.20 | 5796.00 | 6839.28 | 3090.00 | Power Tools and Engineering | 3646.20 | Power Tools and Engineering
14.03 | Supplying and fixing following piano type switch/ socket on the existing switch box/ cover including connections etc. as required: 15/16 A switch | 3.00 | Each | item31 | 213.00 | 251.34 | 336.00 | 396.48 | 213.00 | Power Tools and Engineering | 251.34 | Power Tools and Engineering
14.04 | Supplying and fixing following piano type switch/ socket on the existing switch box/ cover including connections etc. as required: 6 pin 15/16 A socket outlet | 3.00 | Each | item32 | 267.00 | 315.06 | 393.00 | 463.74 | 267.00 | Power Tools and Engineering | 315.06 | Power Tools and Engineering
15.00 | Light Fixture
15.01 | Supply of LED tubelight,Decorative,Ultraslim linear LED fixture with tube | 6.00 | Nos | item33 | 3000.00 | 3540.00 | 2646.00 | 3122.28 | 2646.00 | BORA ELECTRICALS | 3122.28 | BORA ELECTRICALS
| Total in Figures |  |  |  | 2973767.00 | 3509045.06 | 2995896.00 | 3535157.28