## BoQ1
Government eProcurement System Created By: Ajit Kumar Created Date/Time: 06-Oct-2026 03:38 PM Tender Title: Electrical Works at the Newly Shifted PSA near the MSAA#EPS Tender ID: 2026_ONGC_291324_1
Tender Inviting Authority: Engineering Services, ONGC Rajahmundry Asset
Name of Work: Electrical Works at the Newly Shifted PSA near the MSAA#EPS
Tender No: KE1AL26014
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | VENUS INDUSTRIES (GSTN-NA) BID ID -1075942 |  | VIJAYA ELECTRICAL AND REWINDING WORKS (GSTN-NA) BID ID -1073887 |  | CORNERSTONE ENGINEERING AND SERVICES (GSTN-NA) BID ID -1072943
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Description
1.01 | Foundation and Erection charges for 7.5Mtr length metallic pole duly erecting on base plate with providing 4 Nos, Anchor bolts with providing of 1:3:6 CC foundation (as per the drawing) with necessary steel reinforcement work, embedding 32mm G.I. pipe in pole collar/ foundation (during casting) including bending the pipe to the required shape for cable entry, curing, all material and labour charges, including excavation of Earth etc. as per the EIC instructions | 16.00 | Nos. |  | 5650.00 | 106672.00 | 5500.00 | 103840.00 | 5000.50 | 94409.44 | 94409.44 | CORNERSTONE ENGINEERING AND SERVICES
1.02 | Providing and Fixing of Junction Box Support adjacent to Light Pole Foundation; Providing, fabricating, and fixing a vertical support for mounting the Junction Box adjacent to the light pole foundation, made of MS L-Angle of size 35x35x5mm and length 2 feet (0.6 m), grouted in concrete to a depth of 1 foot below ground level, with 1 foot projecting above ground level. A horizontal MS L-Angle piece of the same size (35x35x5mm), 200 mm long, shall be welded to the vertical support at the appropriate height, on which the Junction Box shall be mounted using suitable mounting accessories. The complete fabricated assembly shall be finished with silver epoxy paint. Note: JB will be provided by ONGC | 16.00 | Nos. |  | 1000.00 | 18880.00 | 900.00 | 16992.00 | 750.00 | 14160.00 | 14160.00 | CORNERSTONE ENGINEERING AND SERVICES
1.03 | Supplying and fixing of 32 mm dia X 2.00 metres long G.I. pipe (medium class) bracket for mounting of fluorescent / HPMV / HPSV street light fitting on pole including bending the pipe to the required shape, 2 nos 40 mm X 3 mm flat iron clamps with nuts, bolts and washer, painting the flat iron with primer and finish paint etc. as required. | 13.00 | Nos. |  | 1450.00 | 22243.00 | 1500.00 | 23010.00 | 1250.00 | 19175.00 | 19175.00 | CORNERSTONE ENGINEERING AND SERVICES
1.04 | Earthing with G.I. earth pipe 3.0 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 14.00 | Nos. |  | 6620.00 | 109362.40 | 6500.00 | 107380.00 | 6089.83 | 100603.99 | 100603.99 | CORNERSTONE ENGINEERING AND SERVICES
1.05 | Supplying and laying 25 mm X 3 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 420.00 | Mtr |  | 135.00 | 66906.00 | 140.00 | 69384.00 | 135.59 | 67198.40 | 66906.00 | VENUS INDUSTRIES
1.06 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required for light pole earthing | 150.00 | Mtr |  | 65.00 | 11505.00 | 55.00 | 9735.00 | 52.54 | 9299.58 | 9299.58 | CORNERSTONE ENGINEERING AND SERVICES
1.07 | Providing and fixing 10 Sq.MM green flexible cable for loop earthing as required along with lugs | 100.00 | Mtr |  | 162.00 | 19116.00 | 150.00 | 17700.00 | 146.61 | 17299.98 | 17299.98 | CORNERSTONE ENGINEERING AND SERVICES
1.08 | Laying of PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size up to Upto 35 sq. mm direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. | 800.00 | Mtr |  | 405.00 | 382320.00 | 390.00 | 368160.00 | 383.90 | 362401.60 | 362401.60 | CORNERSTONE ENGINEERING AND SERVICES
1.09 | Laying of additional PVC insulated and PVC sheathed / XLPE power cables of 1.1 KV grade of size up to 25 Sq. MM Cable in the existing masonry duct.trench as required. | 800.00 | Mtr |  | 37.00 | 34928.00 | 32.00 | 30208.00 | 30.51 | 28801.44 | 28801.44 | CORNERSTONE ENGINEERING AND SERVICES
1.10 | Route Marker Supplying and fixing cable route marker with 10 cm X 10 cm X 5 mm thick G.I. plate with inscription there on, bolted /welded to 35 mm X 35 mm X 6 mm angle iron, 60 cm long and fixing the same in ground as required. Route markers to be placed at a distance of 30 Mtr along straight path with closer interval ( or at every bend/joint) in conjested or turning areas. | 10.00 | Nos. |  | 500.00 | 5900.00 | 520.00 | 6136.00 | 506.78 | 5980.00 | 5900.00 | VENUS INDUSTRIES
1.11 | Cable End termination: Supply and making one end termination with heavy duty single compression brass gland as per BS 6121:2005 ,IP 66 complete, SIBG type, heavy duty Alluminium lugs duly crimped with crimping tool, PVC tape etc for 4core 16sqmm size of Armoured PVC insulated & PVC sheathed/XLPE aluminium conductor cable of 1100 volt grade as required of size. | 160.00 | Nos. |  | 100.00 | 18880.00 | 105.00 | 19824.00 | 103.00 | 19446.40 | 18880.00 | VENUS INDUSTRIES
1.12 | Wiring for circuit/ submain wiring alongwith earth wire with 3Cx1.5Sq.MM PVC insulated copper cable in surface/ recessed medium class PVC conduit as required. Individual Light Fixtures Wiring | 350.00 | Mtr |  | 225.00 | 92925.00 | 235.00 | 97055.00 | 266.27 | 109969.51 | 92925.00 | VENUS INDUSTRIES
1.13 | Supply, fixing and Connecting 32 amps, 4 pole RYB Black connector | 16.00 | Nos. |  | 600.00 | 11328.00 | 500.00 | 9440.00 | 72.03 | 1359.93 | 1359.93 | CORNERSTONE ENGINEERING AND SERVICES
1.14 | Supplying and fixing 12 way, single pole and neutral, sheet steel, distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) | 2.00 | Nos. |  | 3000.00 | 7080.00 | 2500.00 | 5900.00 | 2433.05 | 5742.00 | 5742.00 | CORNERSTONE ENGINEERING AND SERVICES
1.15 | Supplying and fixing 63A, four pole, 415 V, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 2.00 | Nos. |  | 1250.00 | 2950.00 | 1000.00 | 2360.00 | 944.92 | 2230.01 | 2230.01 | CORNERSTONE ENGINEERING AND SERVICES
1.16 | Supplying and fixing 32 A rating, SinglePole, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 10.00 | Each |  | 300.00 | 3540.00 | 250.00 | 2950.00 | 241.53 | 2850.05 | 2850.05 | CORNERSTONE ENGINEERING AND SERVICES
1.17 | Wiring for light point/ fan point/ exhaust fan point with 1.5 sq.mm PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box, terminals and earthing the point with 1.5 sq.mm PVC insulated copper conductor single core cable etc. as required. Kitchen Wiring & Walkway Tubelight Wiring | 40.00 | Nos. |  | 1200.00 | 56640.00 | 1050.00 | 49560.00 | 1007.63 | 47560.14 | 47560.14 | CORNERSTONE ENGINEERING AND SERVICES
1.18 | Wiring for circuit/ submain wiring along with earth wire with 2 x 6sqmm + 1x 6sqmm earth wire, PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required. | 30.00 | Mtr |  | 400.00 | 14160.00 | 410.00 | 14514.00 | 408.47 | 14459.84 | 14160.00 | VENUS INDUSTRIES
1.19 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 A & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 6.00 | Nos. |  | 600.00 | 4248.00 | 570.00 | 4035.60 | 558.47 | 3953.97 | 3953.97 | CORNERSTONE ENGINEERING AND SERVICES
1.20 | Supply and fixing of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades with mark. Makes: Crompton / Almounard / Havells Ventil Air-DB | 1.00 | Nos. |  | 4000.00 | 4720.00 | 3500.00 | 4130.00 | 3200.00 | 3776.00 | 3776.00 | CORNERSTONE ENGINEERING AND SERVICES
1.21 | Supplying, Installation, Testing & Commissioning of 70/90Watt Street light LED fixture, powder coated pressure die cast aluminium body | 25.00 | Nos. |  | 2250.00 | 66375.00 | 2500.00 | 73750.00 | 2300.00 | 67850.00 | 66375.00 | VENUS INDUSTRIES
| Total in Figures |  |  |  |  | 1060678.40 |  | 1036063.60 |  | 998527.28
Lowest Amount Quoted BY: CORNERSTONE ENGINEERING AND SERVICES(998527.28)

## BOQ Summary
BOQ Summary Details Tender Title: Electrical Works at the Newly Shifted PSA near the MSAA#EPS Tender ID: 2026_ONGC_291324_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CORNERSTONE ENGINEERING AND SERVICES (BID ID -1072943) | 998527.28 | L1
| 2 | VIJAYA ELECTRICAL AND REWINDING WORKS (BID ID -1073887) | 1036063.60 | L2
| 3 | VENUS INDUSTRIES (BID ID -1075942) | 1060678.40 | L3