## BoQ1
Government eProcurement System Created By: Susmitha Kagitapalli Created Date/Time: 28-Aug-2026 03:23 PM Tender Title: e-tender for Electrical Renovation Work at Basement Area of Main Office Building, New Delhi Tender ID: 2026_RBI_283028_1
Tender Inviting Authority:Estate Department, Reserve Bank of India New Delhi
Name of Work: Electrical Renovation of NAP areas at MOB, RBI, New Delhi
Contract No: 2026_RBI_283028
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Parth Electricals (GSTN-NA) BID ID -1059900 |  | EXCEL ELECTRICALS (GSTN-NA) BID ID -1056934 |  | HARBHAJAN ELECTRIC WORKS (GSTN-NA) BID ID -1060682
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Wiring and Switchboards
1.01 | Lights (Primary) and Fans point Supply, installation, testing and commissioning (SITC) of wiring for tube lights, ceiling fans and exhaust fan point from respective switchboards, using 2 x 1.5 sq mm and 1.0 sq mm, 1100 Volts grade PVC insulated single core multistranded unsheathed copper FRLSH wires, including main circuit wiring from the MCB DB box to respective switchboard in suitable dia medium duty MS conduit with required accessories like bends, tees, junction boxes etc., in partly concealed/ partly surface manner (as the case may be) and making good the chases with cement plaster of suitable thickness, merging with adjoining area. The surface shall be finished by skilled persons for getting a smooth and merging surface. Rate shall include for provision of modular type 10 Amp Switches with 6 Amp Sockets on switchboards (as mentioned above) on factory fabricated GI box (of same Make, as switches plate) and required size mounting plate fixed on respective approved company make boxes concealed in wall. All the fan points need to be terminated on a 3-terminal ceiling rose on a junction box. All tube light points need to be terminated with providing a tee-cover. Necessary circuit wiring from D.B. upto the switch board for above items rate shall be done with (2 x 2.5 and 1 x 1.5) 1100 Volts grade PVC insulated single core multistranded unsheathed copper FRLSH wires. Final connections also shall be made with flexible wires (of suitable rating) etc. Load on each circuit shall not be more than 800 Watts. Use blank plates on switchboards wherever required. | 89.00 | Nos |  | 1525.00 | 160155.50 | 1530.00 | 160680.60 | 1550.00 | 162781.00 | 160155.50 | Parth Electricals
1.02 | Lights (Secondary) Point Same as Item at S.N. 1.01 above, but looped from primary light point, and controlled through same 10 Amp switch of the switchboard. | 14.00 | Nos |  | 760.00 | 12555.20 | 765.00 | 12637.80 | 785.00 | 12968.20 | 12555.20 | Parth Electricals
1.03 | Set of two 6 Amp Plug-point (Primary) SITC of (a pair) independent two 3-pin 6 Amp modular socket controlled by two 10 Amp modular switch housed in metal GI box and modular plate (both of same Make) of suitable size and wired using 2 x 2.5 + 1.5 sq. mm 1100 Volts grade PVC insulated single core multistranded unsheathed copper FRLSH wire, from mains MCB DB laid through recessed medium duty MS conduit pipe complete with all accessories or on surface, as per site requirement as directed by Bank's Engineer. Light & fan switchboard, as per Item 1.01, and Set of two 6 Amp Plug-points, as per Item 1.02, shall be on same main circuit. | 19.00 | Nos | 100.00 | 1690.00 | 37889.80 | 1695.00 | 38001.90 | 1720.00 | 38562.40 | 37889.80 | Parth Electricals
1.04 | Set of two 6 Amp Plug-point (Secondary) SITC of (a pair) independent two 3-pin 6 Amp modular socket controlled by two 10 Amp modular switch housed in metal GI box and modular plate (both of same Make) of suitable size and wired using 2 x 2.5 + 1.5 sq. mm 1100 Volts grade PVC insulated single core multistranded unsheathed copper FRLSH wires, looped from nearest primary point (as per S.N. 1.02) laid through recessed MS medium duty conduit pipe complete with all accessories or on surface, as per site requirement as directed by Bank's Engineer. | 19.00 | Nos | 53.00 | 1690.00 | 37889.80 | 1695.00 | 38001.90 | 1720.00 | 38562.40 | 37889.80 | Parth Electricals
1.05 | Power Plug-point 16 Amp (Primary) SITC of independent 6/16 Amp modular socket controlled by 16 Amp modular switch housed in metal GI box and modular plate (both of same Make) of suitable size and wired using 2 x 2.5 + 1.5 sq. mm 1100 Volts grade PVC insulated single core multistranded unsheathed copper FRLSH wires, from mains MCB DB laid through recessed MS medium duty conduit pipe complete with all accessories or on surface, as per site requirement as directed by Bank's Engineer. | 5.00 | Nos | 10.00 | 4240.00 | 25016.00 | 4250.00 | 25075.00 | 4350.00 | 25665.00 | 25016.00 | Parth Electricals
1.06 | Power Plug-point 16 Amp (Secondary) SITC of independent 6/16 Amp modular socket controlled by 16 Amp modular switch housed in metal GI box and modular plate (both of same Make) of suitable size and wired using 2 x 2.5 + 1.5 sq. mm 1100 Volts grade PVC insulated single core multistranded unsheathed copper FRLSH wires, looped from primary power plug-point laid through recessed MS medium duty conduit pipe complete with all accessories or on surface, as per site requirement as directed by Bank's Engineer. | 4.00 | Nos | 11.00 | 3385.00 | 15977.20 | 3390.00 | 16000.80 | 3350.00 | 15812.00 | 15812.00 | HARBHAJAN ELECTRIC WORKS
1.07 | Plug-point 6 Amp SITC of one 3-pin 6 Amp modular socket controlled by a 10 Amp modular switch, latter housed in metal GI box (both of same Make) and modular plate of suitable size. The wiring to be done using 2 x 2.5 + 1.5 sq. mm PVC insulated single core multistranded unsheathed copper FRLSH wires, extended through switchboard as per S.N. Item 1.01 above, laid through recessed medium duty MS conduit pipe complete with all accessories, or on surface as per site requirement as directed by Bank's Engineer. The socket to be provided at certain height on the wall, while control switch to be provided in the same switchboard as per S.N. Item 1.01 | 10.00 | Nos | 10.00 | 1690.00 | 19942.00 | 1695.00 | 20001.00 | 1725.00 | 20355.00 | 19942.00 | Parth Electricals
1.08 | Regulator Fan regulator: -Supply and fixing of 2 module 4-step electronic regulators 100 watt for BLDC ceiling fans on the existing switch boards of Item No. 1.01 | 35.00 | Nos | 11.00 | 630.00 | 26019.00 | 636.00 | 26266.80 | 650.00 | 26845.00 | 26019.00 | Parth Electricals
2.00 | MCB Distribution System
2.01 | MCB Distribution Box for Lighting, Power & ACs Supply, installation, testing and commissioning of 4-way VTPN MCB DB double-door factory fabricated, IP-43 protection in concealed / surface manner (as per site condition) completes with loop connections, earthing etc. comprising of following MCBs complete as directed. 63 Amps MCCB (10 kA) as Incomer 40A TP (10 kA) C Curve MCB – 3 nos. Blank Plate should be provided wherever required to avoid gaps. All wires shall be terminated using appropriate size lugs. | 1.00 | Nos | 10.00 | 25400.00 | 29972.00 | 25400.00 | 29972.00 | 25500.00 | 30090.00 | 29972.00 | EXCEL ELECTRICALS, Parth Electricals
2.02 | MCB Distribution Box Supply, installation, testing and commissioning of 8-way TPN MCB DB double-door factory fabricated, IP-43 protection in concealed manner, complete with loop connections, earthing etc. comprising of following MCBs as directed by Bank’s Engineer. 40 Amps C-Curve RCBO as incomer with 100 mA sensitivity 10 Amp - 20 Amp SP (10 kA) C-Curve MCB - 14 nos. Blank plate should be provided wherever required to avoid gaps. All wires shall be terminated using appropriate size lugs. | 2.00 | Nos | 22.00 | 7620.00 | 17983.20 | 7625.00 | 17995.00 | 12500.00 | 29500.00 | 17983.20 | Parth Electricals
3.00 | Lighting & Fan Fixtures
3.01 | 4' tube-lights Supply, Installation, testing of min 22 Watts 4 feet LED light fittings (CDL) including connection with insulated copper flexible wire. | 60.00 | Nos | 10.00 | 342.00 | 24213.60 | 340.00 | 24072.00 | 400.00 | 28320.00 | 24072.00 | EXCEL ELECTRICALS
3.02 | 2' tube-lights Supply, Installation, testing of min 10 Watts 2 feet LED light fittings (CDL) including connection with insulated copper flexible wire. | 8.00 | Nos | 22.00 | 330.00 | 3115.20 | 340.00 | 3209.60 | 370.00 | 3492.80 | 3115.20 | Parth Electricals
3.03 | Installing / fixing and commissioning of BLDC ceiling fan of 900 mm / 1200 mm size (as provided by the Bank), on the fan points provided. | 35.00 | Nos | 22.00 | 160.00 | 6608.00 | 170.00 | 7021.00 | 200.00 | 8260.00 | 6608.00 | Parth Electricals
4.00 | Power Cables
4.01 | Mains cable: Supply & laying of 4 core x 25 sq.mm aluminum XPLE armoured cables 1100 V grade along with 2 runs of 12 SWG bare GI wire with all accessories partly over wall/surface and partly in concealed manner/false celling with all necessary accessories like saddle, glands, lugs, cable termination etc from mains panel to MCB board, as directed by Bank’s Engineer. | 50.00 | R.M. | 10.00 | 375.00 | 22125.00 | 380.00 | 22420.00 | 375.00 | 22125.00 | 22125.00 | Parth Electricals, HARBHAJAN ELECTRIC WORKS
4.02 | Sub-mains cable: Supply & laying of 4 core x 16 sq.mm aluminum XPLE armoured cables 1100 V grade along with 2 runs of 12 SWG bare GI wire with all accessories partly over wall/surface and partly in concealed manner/false celling with all necessary accessories like saddle, glands, lugs, cable termination etc from VTPN to TPN MCB boards, as directed by Bank’s Engineer. | 20.00 | R.M. | 22.00 | 335.00 | 7906.00 | 340.00 | 8024.00 | 346.00 | 8165.60 | 7906.00 | Parth Electricals
5.00 | Rebate
5.01 | Rebate after removing / disconnecting Carefully disconnecting / dismantling of existing wiring, electrical switch boards, accessories, and electrical gadgets (like light fixtures, ceiling fans, wall fans, exhaust fans, etc.) and keep it in Bank's custody in proper manner, followed by taking away, old non-usable removed MCBs, DPs, conduits, wires, switchboards etc, by offering rebate amount. (L.S.) | 1.00 | Nos | 10.00 | 2000.00 | 4360.00 | 500.00 | 1090.00 | 1500.00 | 3270.00 | 1090.00 | EXCEL ELECTRICALS
| Total in Figures |  |  |  |  | 451727.50 |  | 450469.40 |  | 474774.40
Lowest Amount Quoted BY: EXCEL ELECTRICALS(450469.40)

## BOQ Summary
BOQ Summary Details Tender Title: e-tender for Electrical Renovation Work at Basement Area of Main Office Building, New Delhi Tender ID: 2026_RBI_283028_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | EXCEL ELECTRICALS (BID ID -1056934) | 450469.40 | L1
| 2 | Parth Electricals (BID ID -1059900) | 451727.50 | L2
| 3 | HARBHAJAN ELECTRIC WORKS (BID ID -1060682) | 474774.40 | L3